## 2025 DTAPR FINAL
Location | Feeder Name | Type of risk | Year Identified | Rating (Amps) | 2024/25 Load (11kV amps) | 25/26 N-1 Load at Risk (11kV Amps) | 26/27 N-1 Load at Risk (11kV Amps) | 27/28 N-1 Load at Risk (11kV Amps) | Forecast Risk Year | Potential Solution
Speers Point | ARGENTON 132/11 PA11 | N-1 | 2024 | 400 | 322 | 179 | 179 | 179 | Existing | Under investigation
Macmasters Beach | AVOCA PA24 | N-1 | 2024 | 280 | 158 | 45 | 45 | 45 | Existing | Under investigation
Macmasters Beach | AVOCA PA33 | N-1 | 2024 | 325 | 156 | 21 | 21 | 21 | Existing | Under investigation
Punchbowl | BANKSTOWN PA10 | N-1 | 2025 | 300 | 174 | 50 | 50 | 50 | Existing | Under investigation
Brooklyn / Somersby | BEROWRA PA11 | N-1 | 2025 | 350 | 86 | 32 | 32 | 32 | Existing | Project in delivery
Cowan | BEROWRA PA21 | N-1 | 2025 | 350 | 189 | 104 | 104 | 104 | Existing | Under investigation
Blakehurst | BLAKEHURST PA1 | N-1 | 2025 | 355 | 186 | 156 | 156 | 156 | Existing | Under investigation
Blakehurst | BLAKEHURST PA12 | N-1 | 2025 | 355 | 179 | 90 | 90 | 90 | Existing | Under investigation
Branxton | BRANXTON 66 PA13 | N-1 | 2024 | 400 | 232 | 85 | 85 | 85 | Existing | Project under development
Burwood | BURWOOD PA09 | N-1 | 2025 | 390 | 266 | 53 | 53 | 53 | Existing | Under investigation
Canada Bay | BURWOOD PA19 | N-1 | 2025 | 400 | 158 | 136 | 136 | 136 | Existing | Under investigation
Cardiff | CARDIFF 33 PA01 | N-1 | 2025 | 301 | 236 | 46 | 46 | 46 | Existing | Under investigation
Warners Bay | CARDIFF 33 PA12 | N-1 | 2025 | 301 | 208 | 22 | 22 | 22 | Existing | Under investigation
Cardiff | CARDIFF 33 PA16 | N-1 | 2025 | 301 | 245 | 80 | 80 | 80 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA02 | N-1 | 2024 | 335 | 275 | 180 | 180 | 180 | Existing | Under investigation
Cessnock | CESSNOCK SOUTH PA07 | N-1 | 2025 | 305 | 203 | 60 | 60 | 60 | Existing | Under investigation
Charlestown | CHARLESTOWN 132 PA08 | N-1 | 2025 | 400 | 384 | 119 | 119 | 119 | Existing | Under investigation
Woongarrah | CHARMHAVEN PA01 | N-1 | 2024 | 355 | 314 | 38 | 38 | 38 | Existing | Project in delivery
Hamlyn Terrace | CHARMHAVEN PA09 | N-1 | 2025 | 305 | 255 | 104 | 104 | 104 | Existing | Project under development
Woongarrah | CHARMHAVEN PA10 | N-1 | 2025 | 315 | 224 | 66 | 66 | 66 | Existing | Project under development
Woongarrah | CHARMHAVEN PA12 | N-1 | 2025 | 370 | 120 | 0 | 72 | 72 | 2026 | Project in delivery
Lane Cove | CHATSWOOD PA37 | N-1 | 2025 | 320 | 164 | 194 | 194 | 194 | Existing | Project under development
Lane Cove | CHATSWOOD PA40 | N-1 | 2025 | 400 | 335 | 110 | 110 | 110 | Existing | Project under development
Breakfast Point | CONCORD PA04 | N-1 | 2024 | 320 | 203 | 119 | 119 | 119 | Existing | Project in delivery
Breakfast Point | CONCORD PA17 | N-1 | 2024 | 305 | 180 | 165 | 165 | 165 | Existing | Project in delivery
Breakfast Point | CONCORD PA18 | N-1 | 2024 | 315 | 185 | 79 | 79 | 79 | Existing | Project in delivery
Breakfast Point | CONCORD PA22 | N-1 | 2024 | 315 | 177 | 135 | 135 | 135 | Existing | Project in delivery
Warners Bay | CROUDANCE BAY PA01 | N-1 | 2025 | 282 | 284 | 196 | 196 | 196 | Existing | Under investigation
Valentine | CROUDANCE BAY PA02 | N-1 | 2025 | 373 | 114 | 69 | 69 | 69 | Existing | Under investigation
Belmont | CROUDANCE BAY PA06 | N-1 | 2025 | 373 | 260 | 104 | 104 | 104 | Existing | Under investigation
Valentine | CROUDANCE BAY PA12 | N-1 | 2025 | 337 | 279 | 206 | 206 | 206 | Existing | Under investigation
Pyrmont | DARLING HARBOUR 132/11kV PA09 | N-1 | 2025 | 400 | 287 | 40 | 40 | 40 | Existing | Project in delivery
Cameron Park | EDGEWORTH 33 PA01 | N-1 | 2024 | 293 | 293 | 51 | 51 | 51 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA07 | N-1 | 2025 | 258 | 216 | 41 | 41 | 41 | Existing | Under investigation
Cameron Park | EDGEWORTH 33 PA09 | N-1 | 2024 | 263 | 197 | 100 | 100 | 100 | Existing | Under investigation
Holmesville | EDGEWORTH 33 PA10 | N-1 | 2024 | 400 | 359 | 108 | 108 | 108 | Existing | Under investigation
Kilcare | EMPIRE BAY PA08 | N-1 | 2024 | 400 | 176 | 87 | 87 | 87 | Existing | Under investigation
Green Point | ERINA PA01 | N-1 | 2025 | 400 | 195 | 33 | 33 | 33 | Existing | Under investigation
Erina | ERINA PA07 | N-1 | 2025 | 400 | 266 | 123 | 123 | 123 | Existing | Under investigation
Erina | ERINA PA13 | N-1 | 2025 | 280 | 173 | 35 | 35 | 35 | Existing | Under investigation
Homebush | FLEMINGTON PA04 | N-1 | 2025 | 300 | 185 | 175 | 175 | 175 | Existing | Project under development
Putney | HUNTERS HILL PA36 | N-1 | 2025 | 340 | 158 | 50 | 50 | 50 | Existing | Under investigation
Riverview | HUNTERS HILL PA41 | N-1 | 2025 | 330 | 155 | 47 | 47 | 47 | Existing | Under investigation
Riverview | HUNTERS HILL PA57 | N-1 | 2025 | 315 | 159 | 38 | 38 | 38 | Existing | Under investigation
Woronora | JANNALI PA25 | N-1 | 2025 | 315 | 121 | 53 | 53 | 53 | Existing | Under investigation
Kurri Kurri | KURRI 132/11kV PA06 | N-1 | 2024 | 400 | 242 | 162 | 162 | 162 | Existing | Under investigation
Heddon Greta | KURRI 132/11kV PA12 | N-1 | 2025 | 400 | 306 | 50 | 50 | 50 | Existing | Under investigation
Gillieston Heights | KURRI 132/11kV PA19 | N-1 | 2024 | 400 | 329 | 115 | 115 | 115 | Existing | Under investigation
Summerland Point | LAKE MUNMORAH PA07 | N-1 | 2024 | 390 | 382 | 152.3997 | 152 | 152 | Existing | Under investigation
Bateau Bay | LONG JETTY PA02 | N-1 | 2024 | 280 | 176 | 145 | 145 | 145 | Existing | Under investigation
Maitland Vale | MAITLAND 33 PA04 | N & N-1 | 2024 | 270 | 291 | 240 | 240 | 240 | Existing | Project under development
Aberglasslyn | MAITLAND 33 PA07 | N & N-1 | 2024 | 290 | 310 | 249 | 249 | 249 | Existing | Project under development
Largs | MAITLAND 33 PA11 | N & N-1 | 2024 | 260 | 257 | 133 | 133 | 133 | Existing | Project under development
Bolwarra Heights | MAITLAND 33 PA13 | N-1 | 2024 | 260 | 226 | 193 | 193 | 193 | Existing | Project under development
Fletcher | MARYLAND 132 PA02 | N-1 | 2024 | 384 | 238 | 67 | 67 | 67 | Existing | Under investigation
Fletcher | MARYLAND 132 PA06 | N-1 | 2024 | 384 | 290 | 53 | 53 | 53 | Existing | Under investigation
Cameron Park | MARYLAND 132 PA10 | N-1 | 2024 | 400 | 102 | 26 | 26 | 26 | Existing | Under investigation
Muswellbrook | MITCHELL LINE 66 PA11 | N-1 | 2024 | 400 | 199 | 100 | 100 | 100 | Existing | Project under development
Wyee | MORISSET 132 PA06 | N-1 | 2024 | 364 | 251 | 64 | 64 | 64 | Existing | Project under development
Mosman | MOSMAN PA36 | N-1 | 2025 | 350 | 112 | 26 | 26 | 26 | Existing | Under investigation
Eleebana | MT HUTTON PA03 | N-1 | 2025 | 288 | 255 | 53 | 53 | 53 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA03 | N-1 | 2025 | 398 | 163 | 31 | 31 | 31 | Existing | Under investigation
Soldiers Point | NELSON BAY 33 PA04 | N-1 | 2024 | 282 | 232 | 109 | 109 | 109 | Existing | Under investigation
Nelson Bay | NELSON BAY 33 PA05 | N-1 | 2025 | 263 | 211 | 124 | 124 | 124 | Existing | Under investigation
Anna Bay | NELSON BAY 33 PA09 | N-1 | 2025 | 385 | 147 | 183 | 183 | 183 | Existing | Under investigation
Bar Beach | NEWCASTLE CBD 33 PA30 | N-1 | 2024 | 265 | 241 | 26 | 26 | 26 | Existing | Under investigation
Cessnock | NULKABA 33 PA05 | N-1 | 2025 | 400 | 277 | 93 | 93 | 93 | Existing | Under investigation
Homebush | OLYMPIC PARK PA06 | N-1 | 2025 | 400 | 184 | 88 | 88 | 88 | Existing | Project under development
Homebush | OLYMPIC PARK PA10 | N-1 | 2025 | 400 | 108 | 121 | 121 | 121 | Existing | Project under development
Blacksmiths | PELICAN 33 PA01 | N-1 | 2025 | 400 | 178 | 46 | 46 | 46 | Existing | Under investigation
Rathmines | RATHMINES 132 PA10 | N-1 | 2024 | 288 | 197 | 180 | 180 | 180 | Existing | Under investigation
Raymond Terrace | RAYMOND TERRACE 33 PA04 | N-1 | 2025 | 308 | 51 | 20 | 20 | 20 | Existing | Under investigation
Rose Bay | ROSE BAY PA13 | N-1 | 2025 | 290 | 195 | 78 | 78 | 78 | Existing | Under investigation
Aberglasslyn | RUTHERFORD 33 PA02 | N & N-1 | 2024 | 350 | 447 | 396 | 396 | 396 | Existing | Project under development
Rutherford | RUTHERFORD 33 PA03 | N-1 | 2024 | 380 | 281 | 36 | 36 | 36 | Existing | Project under development
Rutherford | RUTHERFORD 33 PA09 | N-1 | 2024 | 350 | 161 | 151 | 151 | 151 | Existing | Project under development
Whittingham / Abattoir | SINGLETON 66 PA28 | N-1 | 2024 | 400 | 244 | 145 | 145 | 145 | Existing | Under investigation
Kariong | SOMERSBY PA16 | N-1 | 2025 | 295 | 219 | 32 | 32 | 32 | Existing | Under investigation
Somersby | SOMERSBY PA17 | N-1 | 2024 | 295 | 85 | 63 | 63 | 63 | Existing | Under investigation
Redfern | ST. PETERS PA20 | N-1 | 2025 | 400 | 212 | 28 | 28 | 28 | Existing | Under investigation
Erskineville | ST. PETERS PA32 | N-1 | 2025 | 316 | 197 | 45 | 45 | 45 | Existing | Under investigation
Tanilba Bay | TANILBA BAY 33 PA15 | N-1 | 2025 | 337 | 176 | 100 | 100 | 100 | Existing | Under investigation
Rutherford | TELARAH 33 PA08 | N-1 | 2024 | 295 | 247 | 156 | 156 | 156 | Existing | Project under development
Rutherford | TELARAH 33 PA10 | N-1 | 2024 | 295 | 203 | 64 | 64 | 64 | Existing | Project under development
Chisholm | THORNTON 33 PA04 | N-1 | 2025 | 383 | 174 | 88 | 88 | 88 | Existing | Project in delivery
Thornton | THORNTON 33 PA11 | N-1 | 2024 | 310 | 223 | 145 | 145 | 190 | Existing | Project in delivery
Thornton | THORNTON 33 PA18 | N-1 | 2024 | 290 | 318 | 196 | 196 | 196 | Existing | Project under development
Chisholm | THORNTON 33 PA20 | N-1 | 2025 | 380 | 252 | 108 | 108 | 348 | Existing | Project in delivery
Tighes Hill / Islington | TIGHES HILL PA09 | N-1 | 2025 | 400 | 144 | 47 | 47 | 47 | 2026 | Project under development
Broadmeadow | TIGHES HILL PA17 | N-1 | 2025 | 400 | 216 | 38 | 38 | 38 | Existing | Project under development
Nelson Bay | TOMAREE 33 PA13 | N-1 | 2025 | 400 | 217 | 75 | 75 | 75 | Existing | Under investigation
Coal Point | TORONTO WEST 132 PA08 | N-1 | 2025 | 335 | 203 | 24 | 24 | 24 | Existing | Under investigation
Gosford | WEST GOSFORD PA03 | N-1 | 2025 | 365 | 168 | 0 | 82 | 163 | 2026 | Under investigation
Gosford | WEST GOSFORD PA12 | N-1 | 2025 | 400 | 305 | 28 | 28 | 28 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA01 | N-1 | 2025 | 224 | 122 | 246 | 246 | 246 | Existing | Project in delivery
Fern Bay | WILLIAMTOWN PA02 | N-1 | 2025 | 148 | 13 | 103 | 103 | 103 | Existing | Under investigation
Williamtown | WILLIAMTOWN PA04 | N-1 | 2025 | 484 | 29 | 0 | 80 | 160 | 2026 | Project in delivery
Saratoga | WOY WOY PA06 | N-1 | 2025 | 290 | 58 | 32 | 32 | 32 | Existing | Under investigation
Warnervale | WYONG PA03 | N-1 | 2025 | 285 | 106 | 50 | 100 | 100 | Existing | Project under development
Jilliby | WYONG PA05 | N-1 | 2024 | 285 | 220 | 76.4993 | 76 | 76 | Existing | Project under development
Tacoma | WYONG PA10 | N-1 | 2024 | 355 | 238 | 216.415 | 216 | 216 | Existing | Project under development
Wyong Creek | WYONG PA12 | N-1 | 2024 | 370 | 120 | 74.248 | 74 | 74 | Existing | Project under development
Jilliby | WYONG PA14 | N-1 | 2025 | 400 | 183 | 217 | 217 | 217 | Existing | Project under development
Waterloo | ZETLAND PA10 | N-1 | 2025 | 355 | 186 | 26 | 26 | 26 | Existing | Project under development