## Appendix C.1_Dist services
Export Data (MW) - Zone Substation
Name | Hrs above 95% export | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
ABERDEEN | 8 | 1.278 | 1.4177 | 1.581 | 1.7274 | 1.863 | 1.9998
ADAMSTOWN | 7.5 | 5.4243 | 6.2891 | 7.2989 | 8.2115 | 9.0593 | 9.9192
ARGENTON | 4 | 7.9388 | 8.8666 | 9.9503 | 10.9004 | 11.7594 | 12.6038
AUBURN | 3.5 | 1.414 | 1.6586 | 1.9432 | 2.3093 | 2.7624 | 3.3121
AVOCA | 5.5 | 8.9261 | 10.3591 | 12.0345 | 13.4417 | 14.6415 | 15.7699
AVONDALE | 5 | 4.1684 | 4.4833 | 4.8513 | 5.1557 | 5.411 | 5.6459
BAERAMI | 4 | 0.10636 | 0.1233 | 0.14307 | 0.16414 | 0.18716 | 0.21334
BALGOWLAH NORTH | 3 | 5.3761 | 6.3669 | 7.5259 | 8.5164 | 9.379 | 10.2084
BANKSTOWN | 2.5 | 6.8363 | 8.0042 | 9.3671 | 10.7385 | 12.1554 | 13.7119
BASS HILL | 6 | 1.9768 | 2.4486 | 3.0003 | 3.4609 | 3.8519 | 4.2168
BEACON HILL | 2.5 | 2.891 | 3.4242 | 4.0469 | 4.6081 | 5.1319 | 5.6606
BELMORE PARK | 0.5 | 0.11661 | 0.22843 | 0.35807 | 0.56727 | 0.85887 | 1.2302
BELROSE | 6.5 | 5.2634 | 6.198 | 7.2914 | 8.1341 | 8.7726 | 9.2978
BERKELEY VALE | 2.5 | 6.8867 | 7.721 | 8.695 | 9.591 | 10.4454 | 11.3235
BEROWRA | 7 | 5.2605 | 6.1767 | 7.2485 | 8.0901 | 8.7467 | 9.3066
BLACKWATTLE BAY | 7 | 0 | 0 | 0 | 0 | 0 | 0
BLAKEHURST | 9.5 | 3.4064 | 4.1395 | 4.9961 | 5.8051 | 6.5893 | 7.4162
BOTANY | 3.5 | 2.4129 | 2.9381 | 3.5504 | 4.2238 | 4.9731 | 5.834
BRANDY HILL | 4 | 3.6131 | 3.9052 | 4.2471 | 4.5076 | 4.7019 | 4.8584
BRANXTON | 4.5 | 5.0486 | 5.4704 | 5.9637 | 6.359 | 6.6766 | 6.9564
BROADMEADOW | 4.5 | 3.6976 | 4.2135 | 4.8149 | 5.4127 | 6.0253 | 6.6917
BROOKVALE | 7.5 | 2.9309 | 3.5065 | 4.177 | 5.075 | 6.2081 | 7.6056
BURWOOD | 4 | 5.0365 | 6.2893 | 7.7513 | 9.3135 | 11.0107 | 12.9357
CAMPBELL ST | 2 | 0.4497 | 0.98116 | 1.5994 | 2.4802 | 3.6285 | 5.0644
CAMPERDOWN | 6.5 | 0.65149 | 0.96985 | 1.3407 | 1.8038 | 2.3624 | 3.0368
CAMPSIE | 9.5 | 7.0006 | 8.898 | 11.1129 | 13.2488 | 15.3657 | 17.6289
CARDIFF | 3.5 | 4.8971 | 5.4862 | 6.1744 | 6.7774 | 7.3213 | 7.8568
CAREEL BAY | 4 | 1.844 | 2.3789 | 3.0043 | 3.5161 | 3.9384 | 4.3223
CARINGBAH | 8 | 1.973 | 2.4708 | 3.0519 | 3.7141 | 4.4696 | 5.3546
CASTLE COVE | 3.5 | 5.0708 | 6.2955 | 7.7259 | 9.1412 | 10.5868 | 12.1575
CESSNOCK SOUTH | 1 | 11.9413 | 13.3259 | 14.9442 | 16.2885 | 17.4212 | 18.4705
CHARLESTOWN | 5 | 6.0531 | 7.0588 | 8.2334 | 9.2649 | 10.1956 | 11.1135
CHARMHAVEN | 7 | 13.566 | 14.9289 | 16.5213 | 17.8213 | 18.8907 | 19.857
CHATSWOOD | 3 | 3.8016 | 4.7269 | 5.8077 | 6.9323 | 8.125 | 9.4618
CITY CENTRAL | 1.5 | 0.4717 | 0.4717 | 0.4717 | 0.4717 | 0.4717 | 0.4717
CITY EAST | 2 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
CITY NORTH | 7 | 1.0791 | 1.0791 | 1.0791 | 1.0791 | 1.0791 | 1.0791
CITY SOUTH | 0.5 | 0.20686 | 1.4419 | 2.874 | 5.2704 | 8.6511 | 12.9955
CLOVELLY | 4 | 2.268 | 2.9493 | 3.7443 | 4.6708 | 5.7366 | 6.996
CONCORD | 2.5 | 3.8322 | 4.6476 | 5.5992 | 6.6346 | 7.773 | 9.0762
CRONULLA | 5.5 | 8.377 | 10.0427 | 11.9913 | 13.7125 | 15.2686 | 16.8188
CROUDACE BAY | 4.5 | 6.3826 | 7.045 | 7.8193 | 8.4541 | 8.9795 | 9.458
CROWS NEST | 4.5 | 1.5401 | 2.1775 | 2.9205 | 3.8686 | 5.0287 | 6.4409
CROYDON | 6 | 3.7798 | 4.614 | 5.5877 | 6.5769 | 7.6039 | 8.7394
DALLEY ST | 1 | 0.11968 | 0.11968 | 0.11968 | 0.11968 | 0.11968 | 0.11968
DARLING HARBOUR | 1 | 0.61671 | 1.0452 | 1.5434 | 2.2767 | 3.247 | 4.4681
DARLINGHURST | 2 | 0.12913 | 0.31514 | 0.53161 | 0.84777 | 1.2635 | 1.7872
DEE WHY WEST | 5 | 5.7406 | 6.9364 | 8.3337 | 9.6878 | 11.0352 | 12.4824
DENMAN | 12.5 | 1.2431 | 1.3917 | 1.5654 | 1.719 | 1.8591 | 1.999
DOUBLE BAY | 5.5 | 1.5356 | 2.4207 | 3.4547 | 4.5535 | 5.7404 | 7.0858
DRUMMOYNE | 3 | 4.2992 | 5.77 | 7.4872 | 9.1957 | 10.9381 | 12.8411
DULWICH HILL |  | 0 | 0 | 0 | 0 | 0 | 0
EDGEWORTH | 5 | 9.0013 | 9.8143 | 10.7641 | 11.538 | 12.1733 | 12.7456
EMPIRE BAY | 6.5 | 3.8956 | 4.4421 | 5.0813 | 5.5788 | 5.961 | 6.2813
ENGADINE | 5.5 | 6.6413 | 7.8588 | 9.283 | 10.4287 | 11.3531 | 12.1728
EPPING | 4 | 5.0308 | 6.0222 | 7.1792 | 8.3983 | 9.706 | 11.177
ERINA | 3 | 4.5983 | 5.4385 | 6.4198 | 7.3224 | 8.1801 | 9.0634
FLEMINGTON | 3 | 2.7223 | 2.9674 | 3.2527 | 3.6045 | 4.0293 | 4.5374
GALSTON | 9 | 2.3192 | 2.6009 | 2.9308 | 3.1965 | 3.4123 | 3.6047
GATESHEAD | 3 | 3.5402 | 4.1703 | 4.9061 | 5.5485 | 6.125 | 6.6901
GORE HILL | 2 | 1.6044 | 1.9926 | 2.4443 | 3.0779 | 3.898 | 4.9192
GREEN SQUARE | 7 | 1.8613 | 2.2732 | 2.7519 | 3.4516 | 4.377 | 5.5384
GREENACRE | 4.5 | 5.4216 | 6.4744 | 7.7029 | 8.9604 | 10.2831 | 11.7477
GREENACRE PARK | 2.5 | 0 | 0 | 0 | 0 | 0 | 0
HARBORD | 6 | 4.1258 | 4.8159 | 5.6223 | 6.3759 | 7.0981 | 7.8542
HOMEBUSH BAY | 2 | 1.0236 | 1.2431 | 1.4982 | 1.8999 | 2.4477 | 3.1458
HORNSBY | 6 | 8.6488 | 10.3294 | 12.2931 | 14.187 | 16.0679 | 18.0795
HUNTERS HILL | 3.5 | 6.5447 | 8.0815 | 9.8784 | 11.4935 | 12.9883 | 14.4987
HURSTVILLE NORTH | 5 | 3.347 | 4.0363 | 4.8407 | 5.6209 | 6.4011 | 7.2372
JANNALI | 5 | 6.3957 | 7.7219 | 9.2741 | 10.4846 | 11.4166 | 12.2021
JESMOND | 4 | 7.2794 | 8.4654 | 9.8506 | 11.0505 | 12.1132 | 13.1466
JEWELLS | 6 | 4.5587 | 5.1345 | 5.8075 | 6.3623 | 6.8252 | 7.25
KILLARNEY | 4.5 | 2.9634 | 3.5062 | 4.1413 | 4.637 | 5.0197 | 5.3426
KINGSFORD | 6.5 | 4.4436 | 5.6385 | 7.0335 | 8.5124 | 10.1009 | 11.8994
KIRRAWEE | 3.5 | 5.1456 | 6.2661 | 7.576 | 8.804 | 9.9911 | 11.2359
KOGARAH | 8.5 | 5.5559 | 7.086 | 8.8712 | 10.7524 | 12.7694 | 15.044
KOTARA | 3.5 | 3.2431 | 3.6449 | 4.1142 | 4.5189 | 4.877 | 5.2229
KURNELL SOUTH | 4.5 | 1.639 | 1.8425 | 2.0802 | 2.2861 | 2.4696 | 2.6481
KURRI | 5 | 9.4631 | 10.4176 | 11.5331 | 12.4422 | 13.1892 | 13.8626
LAKE MUNMORAH | 6.5 | 6.7353 | 7.5224 | 8.4423 | 9.1844 | 9.7852 | 10.3189
LEICHHARDT | 4.5 | 3.3582 | 4.4557 | 5.7358 | 7.0022 | 8.2908 | 9.6903
LEIGHTONFIELD | 3.5 | 2.2573 | 2.6871 | 3.189 | 3.6355 | 4.0453 | 4.4539
LIDCOMBE | 4 | 1.4575 | 1.7638 | 2.1208 | 2.5118 | 2.9454 | 3.4424
LINDFIELD | 3.5 | 5.1117 | 6.2664 | 7.6177 | 8.7321 | 9.6608 | 10.5147
LISAROW | 3 | 4.6876 | 5.3559 | 6.1372 | 6.7795 | 7.3133 | 7.8007
LONG JETTY | 7 | 10.721 | 12.3507 | 14.2544 | 15.9385 | 17.4656 | 18.9855
MACQUARIE PARK | 0.5 | 1.8322 | 2.2708 | 2.781 | 3.437 | 4.2537 | 5.2391
MAITLAND | 6 | 6.1366 | 6.7921 | 7.5578 | 8.2345 | 8.8512 | 9.464
MANLY | 3 | 0.95243 | 1.2604 | 1.6191 | 2.1018 | 2.7094 | 3.4607
MAROUBRA | 4 | 3.2731 | 4.1441 | 5.1601 | 6.2783 | 7.5189 | 8.9463
MARRICKVILLE | 3 | 5.4366 | 6.665 | 8.0969 | 9.622 | 11.2741 | 13.1444
MARYLAND | 8.5 | 14.8756 | 15.818 | 16.9187 | 17.8504 | 18.6537 | 19.4146
MASCOT | 5 | 1.4913 | 2.0105 | 2.6146 | 3.4112 | 4.4086 | 5.6293
MAYFIELD WEST | 2.5 | 3.3637 | 3.7958 | 4.2996 | 4.8124 | 5.3495 | 5.9422
MEADOWBANK | 4.5 | 6.5746 | 8.0303 | 9.7287 | 11.5549 | 13.543 | 15.8073
MEDOWIE | 4.5 | 6.2762 | 6.7727 | 7.3534 | 7.801 | 8.1404 | 8.4196
MENAI | 4 | 13.0714 | 14.9371 | 17.1198 | 18.8148 | 20.1144 | 21.2
MERRIWA | 2 | 0.70714 | 0.82143 | 0.95508 | 1.0644 | 1.1548 | 1.2372
METFORD | 5 | 10.8398 | 11.816 | 12.9567 | 13.9258 | 14.7656 | 15.5656
MILPERRA | 2.5 | 6.7985 | 7.7759 | 8.9173 | 9.9564 | 10.9362 | 11.9346
MIRANDA | 7 | 3.694 | 4.5371 | 5.5231 | 6.381 | 7.1472 | 7.8967
MITCHELL LINE | 4 | 1.9348 | 2.2758 | 2.6747 | 3.0043 | 3.2808 | 3.5355
MITCHELLS FLAT | 2.5 | 0.60687 | 0.66307 | 0.72889 | 0.77782 | 0.81275 | 0.83942
MONA VALE | 4.5 | 4.7344 | 5.594 | 6.5986 | 7.5338 | 8.4329 | 9.3701
MOONAN | 6.5 | 0.11767 | 0.14879 | 0.1851 | 0.22094 | 0.25769 | 0.29744
MORISSET | 3 | 8.5603 | 9.3887 | 10.3566 | 11.1854 | 11.9119 | 12.6101
MORTDALE | 4 | 7.3648 | 8.8554 | 10.5979 | 12.1365 | 13.5279 | 14.912
MOSMAN | 4 | 5.4921 | 7.3217 | 9.4607 | 11.5834 | 13.7415 | 16.099
MOUNT HUTTON | 3.5 | 4.558 | 5.1064 | 5.7477 | 6.2597 | 6.6671 | 7.0239
MUSWELLBROOK | 6.5 | 3.474 | 3.9881 | 4.5892 | 5.1049 | 5.5589 | 5.9966
NARRABEEN | 5 | 2.5076 | 2.9727 | 3.5165 | 3.964 | 4.337 | 4.6781
NELSON BAY | 3.5 | 8.109 | 8.8635 | 9.7443 | 10.5936 | 11.4377 | 12.3387
NEW LAMBTON | 5.5 | 2.5552 | 2.8956 | 3.2933 | 3.6273 | 3.9123 | 4.1799
NEWCASTLE CBD | 4 | 3.5359 | 4.2335 | 5.046 | 6.0685 | 7.3158 | 8.8233
NEWPORT | 5 | 2.2094 | 2.7811 | 3.4496 | 4.0011 | 4.4605 | 4.8829
NORAVILLE | 2.5 | 6.1875 | 7.1089 | 8.1852 | 9.1057 | 9.9092 | 10.6802
NORTH HEAD | 1 | 8.8198 | 8.8198 | 8.8198 | 8.8198 | 8.8198 | 8.8198
NORTH SYDNEY | 13.5 | 1.0666 | 2.0516 | 3.1977 | 4.8444 | 6.9988 | 9.6994
NULKABA | 4 | 3.2543 | 3.631 | 4.0711 | 4.4502 | 4.7856 | 5.1094
OLYMPIC PARK | 2 | 1.6001 | 1.8113 | 2.0572 | 2.3842 | 2.7945 | 3.2982
PADDINGTON | 3 | 0.40577 | 0.93633 | 1.5547 | 2.3389 | 3.2942 | 4.4544
PAXTON | 4.5 | 2.5905 | 2.83 | 3.1101 | 3.3232 | 3.4812 | 3.6079
PEATS RIDGE | 5 | 2.0437 | 2.2144 | 2.4137 | 2.6032 | 2.791 | 2.9885
PELICAN | 12 | 2.615 | 3.0212 | 3.4954 | 3.9352 | 4.3561 | 4.7923
PENNANT HILLS | 6.5 | 15.1131 | 17.5654 | 20.4335 | 22.7343 | 24.585 | 26.2163
PORT BOTANY | 4.5 | 0.45671 | 0.45671 | 0.45671 | 0.45671 | 0.45671 | 0.45671
POTTS HILL | 2.5 | 4.8661 | 5.6725 | 6.6142 | 7.5088 | 8.3848 | 9.3099
PUNCHBOWL | 4 | 4.2605 | 5.3618 | 6.6476 | 7.9272 | 9.231 | 10.6551
PYMBLE | 2 | 3.8216 | 4.6952 | 5.7173 | 6.5958 | 7.369 | 8.1166
RATHMINES | 16 | 5.9926 | 6.662 | 7.4444 | 8.0716 | 8.575 | 9.0181
RAYMOND TERRACE | 3.5 | 5.7082 | 6.4409 | 7.2973 | 8.0249 | 8.6571 | 9.2594
REVESBY | 4.5 | 8.2645 | 9.9715 | 11.967 | 13.6032 | 14.9564 | 16.1887
RIVERWOOD | 6.5 | 4.8799 | 5.8594 | 7.0035 | 8.0606 | 9.0661 | 10.1078
ROCKDALE | 7 | 3.5941 | 4.6817 | 5.9506 | 7.3083 | 8.78 | 10.4526
ROSE BAY | 7.5 | 3.8431 | 5.159 | 6.698 | 8.1562 | 9.575 | 11.0762
ROTHBURY | 12 | 7.379 | 7.6814 | 8.0345 | 8.3532 | 8.6513 | 8.9523
ROUCHEL | 4.5 | 0.13341 | 0.15564 | 0.18161 | 0.20667 | 0.23177 | 0.25873
RUTHERFORD | 3.5 | 8.7058 | 9.3352 | 10.0704 | 10.7147 | 11.2964 | 11.8688
SANS SOUCI | 5 | 2.088 | 2.5701 | 3.1333 | 3.6706 | 4.1961 | 4.7544
SCONE | 7 | 3.7293 | 4.2305 | 4.8166 | 5.3112 | 5.7377 | 6.1418
SEFTON | 5.5 | 8.0732 | 9.6513 | 11.4952 | 13.0974 | 14.5257 | 15.9196
SINGLETON | 1 | 3.0689 | 3.4422 | 3.8783 | 4.273 | 4.6426 | 5.0183
SINGLETON NORTH | 4 | 5.7646 | 6.316 | 6.9614 | 7.4669 | 7.8597 | 8.1933
SOMERSBY | 3 | 5.4583 | 5.8323 | 6.2688 | 6.6801 | 7.0829 | 7.5044
ST IVES | 5.5 | 7.9947 | 9.6438 | 11.5749 | 13.0655 | 14.1967 | 15.1322
ST PETERS | 4.5 | 3.452 | 4.5372 | 5.8011 | 7.2364 | 8.8709 | 10.7733
STOCKTON | 9.5 | 2.5418 | 2.8029 | 3.1075 | 3.3872 | 3.6515 | 3.9229
STRATHFIELD SOUTH | 3.5 | 3.3059 | 4.0096 | 4.8309 | 5.6294 | 6.4303 | 7.2893
SUMMER HILL | 8.5 | 3.3018 | 4.1527 | 5.1453 | 6.1872 | 7.2988 | 8.5496
SURRY HILLS | 1.5 | 4.1255 | 4.1255 | 4.1255 | 4.1255 | 4.1255 | 4.1255
SWANSEA | 8 | 5.4227 | 6.0095 | 6.6949 | 7.2843 | 7.8022 | 8.3026
TANILBA BAY | 7 | 3.8944 | 4.3125 | 4.8011 | 5.2034 | 5.5381 | 5.8446
TARRO | 2.5 | 3.3002 | 3.7127 | 4.1946 | 4.6141 | 4.9899 | 5.3568
TELARAH | 5 | 4.8485 | 5.4045 | 6.0541 | 6.5828 | 7.016 | 7.4059
TERREY HILLS | 2.5 | 1.4527 | 1.6909 | 1.969 | 2.2417 | 2.5197 | 2.8195
THORNTON | 3 | 11.6623 | 12.5835 | 13.6596 | 14.5784 | 15.3823 | 16.1515
TIGHES HILL | 4.5 | 3.0191 | 3.5116 | 4.0856 | 4.674 | 5.2931 | 5.979
TOMALPIN | 6 | 1.3855 | 1.4837 | 1.5977 | 1.7509 | 1.9473 | 2.1867
TOMAREE | 7 | 4.2912 | 4.8227 | 5.4435 | 6.0197 | 6.5703 | 7.1424
TOP RYDE | 3.5 | 5.2303 | 6.3017 | 7.5522 | 8.7707 | 9.9972 | 11.313
TORONTO WEST | 8.5 | 4.7829 | 5.4149 | 6.1532 | 6.7884 | 7.3479 | 7.8886
TURRAMURRA | 4.5 | 4.4958 | 5.667 | 7.0382 | 8.1268 | 8.9895 | 9.7388
UMINA | 8 | 6.869 | 8.208 | 9.7726 | 11.1121 | 12.28 | 13.4032
VALES POINT |  | 0 | 0 | 0 | 0 | 0 | 0
WAMBERAL | 5 | 4.397 | 4.9423 | 5.5804 | 6.0789 | 6.4639 | 6.7892
WAVERLEY | 5 | 2.6017 | 3.5044 | 4.5583 | 5.7311 | 7.0359 | 8.5499
WEST GOSFORD | 2.5 | 6.8366 | 7.9639 | 9.2801 | 10.5937 | 11.945 | 13.4218
WILLIAMTOWN | 11.5 | 1.6016 | 1.7241 | 1.8671 | 1.9965 | 2.1179 | 2.2406
WOY WOY | 4.5 | 3.8364 | 4.5074 | 5.2913 | 5.9896 | 6.6282 | 7.2682
WYONG | 3.5 | 15.8379 | 17.452 | 19.3377 | 20.9595 | 22.3902 | 23.7711
ZETLAND | 3.5 | 1.4878 | 2.0652 | 2.737 | 3.7022 | 4.9604 | 6.538
MATRAVILLE | 1.5 | 8.8755 | 10.4691 | 12.3301 | 14.1224 | 15.8985 | 17.7941
GWAWLEY BAY | 3 | 3.7482 | 4.4894 | 5.3555 | 6.1728 | 6.9701 | 7.8086
RNS HOSPITAL | 7.5 | 0.47045 | 0.61592 | 0.78463 | 1.0377 | 1.3796 | 1.8074
LEMINGTON | 4 | 0.17519 | 0.20981 | 0.25024 | 0.2907 | 0.33269 | 0.37872
MOUNT THORLEY | 4 | 1.9499 | 2.047 | 2.1603 | 2.2701 | 2.3808 | 2.499
NEWDELL | 5 | 0.085507 | 0.12637 | 0.17402 | 0.225 | 0.28118 | 0.34443
GWAWLEY BAY | 3 | 3.7482 | 4.4894 | 5.3555 | 6.1728 | 6.9701 | 7.8086
TOMAGO | 6 | 1.3855 | 1.4837 | 1.5977 | 1.7509 | 1.9473 | 2.1867

## Appendix C.2,C.3_Dist services
Existing Embedded Generating Unit Location | Voltage (kV) | NER S5.8(b)(2A)(vi)* |  |  | NER S5.8(b)(2A)(vii)* |  | NER S5.8(b)(2A)(i) |  | NER S5.8(b)(2A)(ii) |  | NER S5.8(b)(2A)(iii)
|  | Peak MW | MVAr | Hours > 95% Peak | pF | lead / lag | Bulk Supply Point | MW | Feeder | MW | Zone / ST Substation | MW^
Glenbawn | 33 | 0 | 0 | 0 | - | - | Muswellbrook BSP | 0 | 33kV Feeder 89047 | 0 | Muswellbrook STS | 0
HEZ Tomalpin | 33 | 21 | -0.2 | 7.2 | 1 | lagging | Newcastle BSP | 0 | 33kV Feeder KU1(2) | 20.4 | Cessnock South ZS | 20.4
[9 empty] | 33kV Feeder KU1(3) | 20.4 | Tomalpin ZS | 0.6
Glennies Creek | 8.7 | -2.3 | 8.2 | 193.9 | 0.9665 | lagging | Muswellbrook BSP | 0 | 66kV Feeder 6012(5) | 2.9 | Singleton STS | 0
[9 empty] | 66kV Feeder 6012(6) | 2.9
[9 empty] | 66kV Feeder 6012(7) | 5.8
[9 empty] | 66kV Feeder 6012(8) | 8.7
Lucas Heights No1 | 33 | 2.9 | 0.3 | 2641.8 | 0.9947 | leading | Sydney South BSP | 0 | 33kV Feeder 749(1) | 2.9 | Janalli ZS | 2.9
[9 empty] | 33kV Feeder 749(3) | 2.9
Lucas Heights No2 | 33 | 10.8 | 1.1 | 1537.2 | 0.9949 | leading | Sydney South BSP | 0 | 33kV Feeder 732 | 10.8 | Lucas Heights ZS | 6.7
[9 empty] | 33kV Feeder 749(2) | 1.1 | Miranda ZS | 3.1
[9 empty] | 33kV Feeder 750 | 3.1 | Janalli ZS | 1.1
*Based on annual metering data from 1 July 2022 to 1 July 2023, where available
^Excludes figures indicated under EG Export Services_App C.1

## Appendix C.4_Hosting Capacity
Camperdown-Blackwattle Bay Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 581 (Pyrmont STS to Camperdown ZS T3) | 33 | 22 | 0
Feeder 582 (Pyrmont STS to Camperdown ZS T4) | 33 | 22 | 0
Feeder 583 (Pyrmont STS to Camperdown ZS T5) | 33 | 22 | 0
Canterbury-Bankstown Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 648 (Canterbury STS to Campsie ZS T1) | 33 | 31.1 | 0
Feeder 649 (Canterbury STS to Campsie ZS T2) | 33 | 31.1 | 0
Feeder 650 (Canterbury STS to Campsie ZS T3) | 33 | 31.1 | 0
Feeder 642 (Canterbury STS to Summer Hill ZS T1) | 33 | 30.1 | 0
Feeder 646 (Canterbury STS to Summer Hill ZS T2) | 33 | 30.1 | 0
Feeder 647 (Canterbury STS to Summer Hill ZS T3) | 33 | 36.1 | 0
Feeder 632 (Canterbury STS to M5 Tunnel) | 33 | 28.1 | 0
Feeder 633 (Canterbury STS to M5 Tunnel) | 33 | 30.1 | 0
Feeder 655 (Bankstown STS to Bass Hill ZS) | 33 | 35.1 | 32.1
Feeder 661 (Bankstown STS to Bass Hill ZS) | 33 | 44.1 | 33.1
Feeder 665 (Bankstown STS to Punchbowl ZS T13) | 33 | 18.1 | 0
Feeder 666 (Bankstown STS to Punchbowl ZS T14) | 33 | 18.1 | 0
Feeder 667 (Bankstown STS to Punchbowl ZS T12) | 33 | 18.1 | 0
Feeder 668 (Bankstown STS to Punchbowl ZS T11) | 33 | 33.1 | 0
Feeder 282/1 (Sydney South BSP to Revesby ZS) | 132 | 72.1 | 0
Feeder 282/2 (Revesby ZS to Milperra ZS) | 132 | 164.1 | 0
Feeder 283/1 (Sydney South BSP to Revesby ZS) | 132 | 75.1 | 0
Feeder 283/2 (Revesby ZS to Milperra ZS) | 132 | 151.1 | 0
Feeder 735 (Guildford to Leightonfield ZS) | 33 | 55.1 | 40.1
Feeder 736 (Guildford to Leightonfield ZS) | 33 | 54.1 | 40.1
Carlingford Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 813 (Carlingford BSP to Epping ZS) | 66 | 91.1 | 73.1
Feeder 819 (Carlingford BSP to Hunters Hill ZS) | 66 | 109.1 | 86.1
Feeder 820 (Carlingford BSP to Epping ZS) | 66 | 83.1 | 74.1
Feeder 82C (Carlingford BSP to Hunters Hill ZS) | 66 | 73.1 | 73.1
Eastern Suburbs
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 315 (Bunnerong North STS to Matraville ZS T14) | 33 | 15.1 | 0
Feeder 318 (Bunnerong North STS to Matraville ZS T12) | 33 | 17.1 | 0
Feeder 324 (Bunnerong North STS to Matraville ZS T13) | 33 | 18.1 | 0
Feeder 327 (Bunnerong North STS to Mascot ZS T4) | 33 | 16.1 | 0
Feeder 328 (Bunnerong North STS to Mascot ZS T3) | 33 | 16.1 | 0
Feeder 332 (Bunnerong North STS to Mascot ZS T2) | 33 | 15.1 | 0
Feeder 337 (Bunnerong North STS to Mascot ZS T5) | 33 | 15.1 | 0
Feeder 338 (Sydney Airport to International Terminal ) | 33 | 31.1 | 15.1
Feeder 339 (Bunnerong North STS to Port Botany ZS T3) | 33 | 26.1 | 0
Feeder 340 (Bunnerong North STS to Matraville ZS T11) | 33 | 14.1 | 0
Feeder 341 (Bunnerong North STS to Mascot ZS T1) | 33 | 15.1 | 0
Feeder 345 (Bunnerong North STS to Sydney Airport) | 33 | 21.1 | 15.1
Feeder 346 (Bunnerong North STS to Botany ZS T1) | 33 | 12.1 | 0
Feeder 347 (Bunnerong North STS to Port Botany ZS T2) | 33 | 26.1 | 0
Feeder 349 (Bunnerong North STS to Botany ZS T12) | 33 | 14.1 | 0
Feeder 350 (Bunnerong North STS to Botany ZS T2) | 33 | 16.1 | 0
Feeder 352 (Bunnerong North STS to Sydney Airport) | 33 | 18.1 | 15.1
Feeder 353 (Bunnerong North STS to Botany ZS T11) | 33 | 16.1 | 0
Feeder 354 (Bunnerong North STS to Port Botany ZS T1) | 33 | 26.1 | 0
Feeder 355 (Bunnerong North STS to APM) | 33 | 74.1 | 53.1
Feeder 356 (Bunnerong North STS to International Terminal ) | 33 | 23.1 | 15.1
Feeder 358 (Bunnerong North STS to APM) | 33 | 74.1 | 53.1
Feeder 359 (Bunnerong North STS to International Terminal ) | 33 | 23.1 | 15.1
Feeder 360 (Bunnerong North STS to Mascot ZS T6) | 33 | 16.1 | 0
Feeder 376 (Surry Hills STS to Surry Hills ZS T13) | 33 | 29.1 | 0
Feeder 377 (Surry Hills STS to Graving Dock ZS T1) | 33 | 29.1 | 0
Feeder 378 (Surry Hills STS to Graving Dock ZS T2) | 33 | 29.1 | 0
Feeder 380 (Surry Hills STS to Paddington ZS T4) | 33 | 28.1 | 0
Feeder 381 (Surry Hills STS to Paddington ZS T3) | 33 | 28.1 | 0
Feeder 382 (Surry Hills STS to Paddington ZS T2) | 33 | 28.1 | 0
Feeder 383 (Surry Hills STS to Surry Hills ZS T14) | 33 | 26.1 | 0
Feeder 384 (Surry Hills STS to Surry Hills ZS T4) | 33 | 29.1 | 0
Feeder 385 (Surry Hills STS to Surry Hills ZS T3) | 33 | 29.1 | 0
Feeder 386 (Surry Hills STS to Darlinghurst ZS T4) | 33 | 26.1 | 0
Feeder 389 (Surry Hills STS to Darlinghurst ZS T3) | 33 | 26.1 | 0
Inner West Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 200 (Mason Park STSS to Flemington ZS) | 132 | 128.1 | 0
Feeder 201 (Mason Park STSS to Flemington ZS) | 132 | 139.1 | 0
Feeder 606 (Homebush STS to Concord ZS) | 33 | 14.1 | 0
Feeder 607 (Homebush STS to Concord ZS) | 33 | 16.1 | 0
Feeder 608 (Homebush STS to Concord ZS) | 33 | 31.1 | 0
Feeder 609 (Homebush STS to Concord ZS) | 33 | 30.1 | 0
Feeder 61C (Camellia STS to Auburn ZS T3/T4) | 33 | 44.1 | 0
Feeder 61F (Camellia STS to Auburn ZS T5) | 33 | 26.1 | 0
Feeder 61H (Camellia STS to Lidcombe ZS T1/T2) | 33 | 30.1 | 0
Feeder 61G (Camellia STS to Lidcombe ZS T3) | 33 | 30.1 | 0
Feeder 90A (Mason Park STSS to Homebush STS) | 132 | 151.1 | 134.1
Feeder 90G (Mason Park STSS to Olympic Park ZS) | 132 | 183.1 | 155.1
Feeder 90L (Mason Park STSS to Homebush STS) | 132 | 151.1 | 134.1
Feeder 90U (Mason Park STSS to Olympic Park ZS) | 132 | 180.1 | 155.1
Feeder 923 (Mason Park to Burwood ZS) | 132 | 167.1 | 0
Feeder 924 (Mason Park to Burwood ZS) | 132 | 177.1 | 0
Lower North Shore Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 925 (Feeder 925 series reactor to Lindfield STSS) | 132 | 353.1 | 235.1
Feeder 9Y5 (Lindfield STSS to Willoughby STS T 4) | 132 | 233.1 | 225.1
Feeder 9Y7 (Lindfield STSS to Castle Cove ZS) | 132 | 136.1 | 0
Feeder 9E3(1) (Sydney East BSP to Lindfield STSS) | 132 | 317.1 | 246.1
Feeder 9E3(2) (Lindfield STSS to Willoughby STS T3) | 132 | 402.1 | 248.1
Feeder 9E4 (Sydney East BSP to Lindfield STSS) | 132 | 237.1 | 0
Feeder 9Y4 (Lindfield STSS to Willoughby STS T1) | 132 | 237.1 | 0
Feeder 9Y9 (Lindfield STSS to Castle Cove ZS) | 132 | 159.1 | 0
Feeder 9E5(1) (Sydney East BSP to Lindfield STSS) | 132 | 354.1 | 233.1
Feeder 9E5(2) (Lindfield STSS to Willoughby STS T2) | 132 | 322.1 | 235.1
Feeder 9H1 (Willoughby STS to RNSH ZS T1) | 132 | 75.1 | 0
Feeder 9H2 (Willoughby STS to RNSH ZS T2) | 132 | 75.1 | 0
Feeder 9H3 (Willoughby STS to Crows Nest ZS) | 132 | 399.1 | 240.1
Feeder 9H4 (Willoughby STS to Mosman ZS) | 132 | 197 | 0
Feeder 9H5 (Willoughby STS to Crows Nest ZS) | 132 | 368.1 | 240.1
Feeder 9H6 (Willoughby STS to Mosman ZS) | 132 | 197 | 0
Feeder 9P3 (Crows Nest ZS to North Sydney ZS) | 132 | 388.1 | 238.1
Feeder 9P5 (Crows Nest ZS to North Sydney ZS) | 132 | 361.1 | 238.1
Feeder 551 (Willoughby STS to Chatswood ZS T2) | 33 | 55.1 | 0
Feeder 552 (Willoughby STS to Chatswood ZS T1) | 33 | 55.1 | 0
Feeder 554 (Willoughby STS to Chatswood ZS T3) | 33 | 28.1 | 0
Feeder 571 (Willoughby STS to Gore Hill ZS T1) | 33 | 33.1 | 0
Feeder 572 (Willoughby STS to Gore Hill ZS T2) | 33 | 33.1 | 0
Feeder 573 (Willoughby STS to Gore Hill ZS T3) | 33 | 33.1 | 0
Feeder 574 (Willoughby STS to Gore Hill ZS T4) | 33 | 33.1 | 0
Manly Warringah Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 9M1 (Sydney East BSP to Warringah STS) | 132 | 247.1 | 162.1
Feeder 9M2 (Sydney East BSP to Warringah STS) | 132 | 220.1 | 124.1
Feeder 9M3 (Sydney East BSP to Warringah STS) | 132 | 764.1 | 440.1
Feeder 9M4 (Sydney East BSP to Warringah STS) | 132 | 768.1 | 488.1
Feeder 9M5 (Warringah STS to Balgowlah North ZS) | 132 | 218.1 | 0
Feeder S01 (Warringah STS to Balgowlah North ZS) | 33 | 33.1 | 0
Feeder S02(1) (Warringah STS to tee Killarney/Belrose ZS) | 33 | 52.1 | 45.1
Feeder S02(2) (Tee Warringah STS/Killarney/Belrose ZS to Killarney ZS) | 33 | 47.1 | 22.1
Feeder S02(3) (Tee Warringah STS /Killarney/Belrose ZS to Belrose ZS) | 33 | 65.1 | 35.1
Feeder S03(1) (Warringah STS to tee CP Oxford Falls/Belrose ZS) | 33 | 40.1 | 35.1
Feeder S03(2) (Tee Warringah/CP/Belrose ZS to Belrose ZS) | 33 | 58.1 | 35.1
Feeder S05(1) (Warringah STS to Tee CP/Dee Why West ZS) | 33 | 42.1 | 35.1
Feeder S05(2) (Tee Warringah STS/CP/Dee Why West ZS to Dee Why West ZS) | 33 | 61.1 | 35.1
Feeder S06 (Warringah STS to Dee Why West ZS) | 33 | 66.1 | 35.1
Feeder S07(1) (Warringah STS to Tee Brookvale/Harbord ZS) | 33 | 62.1 | 43.1
Feeder S07(2) (Tee Warringah STS/Brookvale/Harbord ZS to Brookvale ZS) | 33 | 41.1 | 0
Feeder S07(3) (Tee Warringah STS/Brookvale/Harbord ZS to Harbord ZS) | 33 | 85.1 | 45.1
Feeder S08(1) (Warringah STS to Tee Manly/Harbord ZS) | 33 | 52.1 | 35.1
Feeder S08(2) (Tee Warringah STS/Manly/Harbord ZS to Manly ZS) | 33 | 66.1 | 40.1
Feeder S08(3) (Tee Warringah STS/Manly/Harbord ZS to Harbord ZS) | 33 | 80.1 | 44.1
Feeder S09 (Warringah STS to Beacon Hill ZS) | 33 | 39.1 | 0
Feeder S10(1) (Warringah STS to Tee Kangaroo Park ) | 33 | 66.1 | 35.1
Feeder S10(3) (Tee Warringah STS to Kangaroo Park Terminal) | 33 | 63.1 | 35.1
Feeder S10(4) (Kangaroo Park Terminal to North Head ZS) | 33 | 30.1 | 21.1
Feeder S10(5) (Kangaroo Park Terminal to Manly ZS) | 33 | 81.1 | 38.1
Feeder S12 (Warringah STS to Beacon Hill ZS) | 33 | 39.1 | 0
Feeder S14 (Warringah STS to Killarney ZS) | 33 | 30.1 | 22.1
Feeder S16 (Warringah STS to Brookvale ZS) | 33 | 29.1 | 29.1
Feeder S17 (Warringah STS to Brookvale ZS) | 33 | 29.1 | 29.1
Feeder S18 (Harbord ZS to North Head ZS) | 33 | 38.1 | 21.1
North West Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 250 (Sydney North to Berowra) | 132 | 306.1 | 248.1
Feeder 251 (Sydney North to Pennant Hills) | 132 | 334.1 | 252.1
Feeder 252 (Berowra to Hornsby) | 132 | 428.1 | 223.1
Feeder 253 (Pennant Hills to Hornsby) | 132 | 364.1 | 254.1
Feeder 257 (Sydney North to Galston) | 132 | 70.1 | 0
Feeder 258 (Sydney North to Galston) | 132 | 70.1 | 0
Pittwater & Terrey Hills Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder S20(1) (Sydney East BSP to S20 Tee1) | 33 | 61.1 | 45.1
Feeder S20(2) (S20 Tee1 to S20 Tee2) | 33 | 85.1 | 45.1
Feeder S20(3) (S20 Tee1 to CP Belrose ZS) | 33 | 35.1 | 0
Feeder S20(4) (S20 Tee2 to Warriewood STSS) | 33 | 62.1 | 45.1
Feeder S20(5) (S20 Tee2 to Narrabeen ZS) | 33 | 40.1 | 0
Feeder S21(1) (Sydney East BSP to S21 Tee1) | 33 | 57.1 | 50.1
Feeder S21(2) (S21 Tee1 to S21 Tee2) | 33 | 78.1 | 53.1
Feeder S21(3) (S21 Tee1 to CP Belrose ZS) | 33 | 52.1 | 0
Feeder S21(4) (S21 Tee 2 to Narrabeen ZS) | 33 | 41.1 | 0
Feeder S21(5) (S21 Tee 2 to Warriewood STSS) | 33 | 87.1 | 54.1
Feeder S22 (Sydney East BSP to Terrey Hills ZS) | 33 | 80.1 | 50.1
Feeder S24 (Sydney East BSP to Terrey Hills ZS) | 33 | 81.1 | 64.1
Feeder S40 (Warriewood STSS to Terrey Hills ZS) | 33 | 73.1 | 45.1
Feeder S42 (Warriewood STSS to Newport ZS) | 33 | 52.1 | 36.1
Feeder S43 (Warriewood STSS to Mona Vale ZS) | 33 | 30.1 | 0
Feeder S44 (Warriewood STSS to Newport ZS) | 33 | 52.1 | 36.1
Feeder S45 (Warriewood STSS to Mona Vale ZS) | 33 | 30.1 | 0
Feeder S46 (Warriewood STSS to Mona Vale ZS) | 33 | 33.1 | 0
Feeder S47 (Newport ZS to Careel Bay ZS) | 33 | 28.1 | 17.1
Feeder S50 (Newport ZS to Careel Bay ZS) | 33 | 31.1 | 17.1
St George Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 670 (Peakhurst STS to Riverwood ZS) | 33 | 25.1 | 0
Feeder 706 (Peakhurst STS to Sans Souci ZS) | 33 | 38.1 | 25.1
Feeder 765 (Peakhurst STS to Mortdale ZS) | 33 | 34.1 | 0
Feeder 769 (Peakhurst STS to Blakehurst ZS) | 33 | 34.1 | 24.1
Feeder 770 (Peakhurst STS to Blakehurst ZS) | 33 | 35.1 | 24.1
Feeder 777 (Blakehurst to Sans Souci ZS) | 33 | 33.1 | 25.1
Feeder 778 (Peakhurst STS to Riverwood ZS) | 33 | 25.1 | 0
Feeder 779 (Peakhurst STS to Riverwood ZS) | 33 | 33.1 | 0
Feeder 785 (Peakhurst STS to Mortdale ZS) | 33 | 34.1 | 0
Feeder 786 (Peakhurst STS to Mortdale ZS) | 33 | 34.1 | 0
Sutherland Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 724 (Port Hacking STS to Miranda ZS) | 33 | 34.1 | 28.1
Feeder 725 (Port Hacking STS to Gwawley Bay ZS) | 33 | 50.1 | 36.1
Feeder 726 (Port Hacking STS to Miranda ZS) | 33 | 41.1 | 29.1
Feeder 728 (Port Hacking STS to Caringbah ZS) | 33 | 41.1 | 36.1
Feeder 730 (Port Hacking STS to Jannali ZS) | 33 | 50.1 | 39.1
Feeder 738 (Port Hacking STS to Jannali ZS) | 33 | 47.1 | 39.1
Feeder 745 (Gwawley Bay ZS to Caringbah ZS) | 33 | 54.1 | 36.1
Feeder 747 (Port Hacking STS to Woronora Dam) | 33 | 43.1 | 0
Feeder 749/1 (Jannali ZS to 749 tee) | 33 | 22.1 | 11.1
Feeder 749/2 (749 tee to Lucas Heights) | 33 | 11.1 | 11.1
Feeder 750 (Lucas Heights ZS to Miranda) | 33 | 11.1 | 4.1
Upper North Shore Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 9E1 (Sydney East BSP to Kuringai STS) | 132 | 332.1 | 251.1
Feeder 9E2 (Sydney East BSP to Kuringai STS) | 132 | 332.1 | 251.1
Feeder 530 (Kuringai STS to Pymble ZS T4) | 33 | 31.1 | 0
Feeder 532 (Kuringai STS to Pymble ZS T2) | 33 | 29.1 | 0
Feeder 533 (Kuringai STS to Pymble ZS T1) | 33 | 29.1 | 0
Feeder 534 (Kuringai STS to Lindfield ZS T2) | 33 | 34.1 | 0
Feeder 535 (Kuringai STS to Lindfield ZS T3) | 33 | 30.1 | 0
Feeder 536/1 (Kuringai STS to Gordon SRA) | 33 | 30.1 | 0
Feeder 536/2 (GORDON SRA to Lindfield ZS T4) | 33 | 30.1 | 0
Feeder 537 (Kuringai STS to Turramurra ZS T1) | 33 | 28.1 | 0
Feeder 538 (Kuringai STS to Turramurra ZS T2) | 33 | 24.1 | 0
Feeder 539 (Kuringai STS to Turramurra ZS T3) | 33 | 22.1 | 0
Feeder 540 (Kuringai STS to St Ives ZS T3) | 33 | 27.1 | 0
Feeder 541 (Kuringai STS to St Ives ZS T2) | 33 | 27.1 | 0
Feeder 542 (Kuringai STS to St Ives ZS T1) | 33 | 27.1 | 0
Lower Central Coast Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 721 - Gosford STS to Lisarow ZS | 33 | 38.1 | 0
Feeder 757 - Peats Ridge ZS to Mangrove Creek PS 33kV | 33 | 23.1 | 0
Feeder 794 - Ourimbah STS to Peats Ridge ZS | 33 | 29.1 | 0
Feeder 824(1) - Gosford STS to 824 Tee 1 | 66 | 106.1 | 72.1
Feeder 824(2) - 824 Tee 1 to Erina ZS | 66 | 119.1 | 72.1
Feeder 824(4) - 824 Tee 2 to Wamberal ZS | 66 | 26.1 | 0
Feeder 824(5) - 824 Tee 2 to Avoca ZS | 66 | 130.1 | 73.1
Feeder 826 - Gosford STS to Erina ZS | 66 | 112.1 | 71.1
Feeder 828 - Gosford STS to Woy Woy ZS | 66 | 140.1 | 61.1
Feeder 830 - Gosford STS to Umina ZS | 66 | 124.1 | 64.1
Feeder 840 - Umina ZS to Woy Woy ZS | 66 | 95.1 | 56.1
Feeder 841 - Erina ZS to Avoca ZS | 66 | 92.1 | 62.1
Feeder 883 - Avoca ZS to Empire Bay ZS | 66 | 87.1 | 0
Feeder 88J - Ourimbah STS to Long Jetty ZS | 66 | 146.1 | 65.1
Feeder 88M - Ourimbah STS to Long Jetty ZS | 66 | 80.1 | 56.1
Upper Central Coast Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 743/1 - Munmorah STS Tx2 to 743 Tee 1 | 33 | 54 | 0
Feeder 743/2 - 743 Tee 1 to Vales Point ZS | 33 | 29 | 0
Feeder 743/3 - 743 Tee 1 to Noraville ZS | 33 | 51 | 0
Feeder 744/1 - Munmorah STS Tx1 to 744 Tee 1 | 33 | 49 | 0
Feeder 744/2 - 744 Tee 1 to Vales Point ZS | 33 | 29 | 0
Greater Cessnock Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder KU1(1) - Kurri STS to KU1 Tee | 33 | 30.1 | 14.1
Feeder KU1(2) - KU1 Tee to Tomalpin ZS | 33 | 20.1 | 0
Feeder KU1(3) - KU1 Tee to Cessnock South ZS | 33 | 45.1 | 14.1
Feeder KU6(1) - Kurri STS to KU6 Tee 1 | 33 | 56.1 | 38.1
Feeder KU6(2) - KU6 Tee 1 to P:GS-71135 | 33 | 48 | 0
Feeder KU6(3) - KU6 Tee 1 to KU6 Tee 2 | 33 | 80.1 | 42.1
Feeder KU6(4) - KU6 Tee 2 to Nulkaba ZS | 33 | 81.1 | 48.1
Feeder KU6(5) - KU6 Tee 2 to Cessnock South ZS | 33 | 60.1 | 25.1
Feeder KU9(1) - Kurri STS to KU9 Tee | 33 | 57.1 | 42.1
Feeder KU9(2) - KU9 Tee to Nulkaba ZS | 33 | 83.1 | 42.1
Feeder 30092(1) - Cessnock South ZS to 30092 Tee 1 | 33 | 22.1 | 0
Feeder 30092(2) - 30092 Tee 1 to LB-30195 | 33 | 21.1 | 0
Feeder 30092(3) - 30092 Tee 1 to 30092 Tee 2 | 33 | 22.1 | 0
Feeder 30092(4) - 30092 Tee 3 to LB-10011 | 33 | 13.1 | 0
Feeder 30092(5) - 30092 Tee 3 to 30092 Tee 4 | 33 | 14.1 | 0
Feeder 30092(6) - 30092 Tee 2 to 30092 Tee 3 | 33 | 14.1 | 0
Feeder 30092(7) - 30092 Tee 2 to Austar Kitchener 33kV | 33 | 20.1 | 0
Feeder 30092(8) - 30092 Tee 4 to Paxton Tx1 | 33 | 14.1 | 0
Feeder 30092(9) - 30092 Tee 4 to Paxton Tx2 | 33 | 14.1 | 0
Feeder 30095(1) - Cessnock South ZS to 30095 Tee 1 | 33 | 20.1 | 0
Feeder 30095(2) - 30095 Tee 1 to LB-30195 | 33 | 20.1 | 0
Feeder 30095(3) - 30095 Tee 1 to 30095 Tee 2 | 33 | 20.1 | 0
Feeder 30095(4) - 30095 Tee 2 to Austar Ellalong 33kV | 33 | 13.1 | 0
Feeder 30095(5) - 30095 Tee 2 to LB-10011 | 33 | 20.1 | 0
Maitland Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder KU2 - Kurri STS to Bloomfield Colliery 33kV | 33 | 20.1 | 0
Feeder KU3(1) - Kurri STS to KU3 Tee 1 | 33 | 46.1 | 20.1
Feeder KU3(2) - KU3 Tee 1 to LB-77994 | 33 | 22.1 | 18.1
Feeder KU4(1) - Kurri STS to KU4 Tee 1 | 33 | 59.1 | 38.1
Feeder KU4(2) - KU4 Tee 1 to Rutherford ZS | 33 | 53.1 | 30.1
Feeder KU4(3) - KU4 Tee 1 to Maitland ZS | 33 | 57.1 | 25.1
Feeder KU5 - Kurri STS to Telarah ZS | 33 | 23.1 | 18.1
Feeder KU8 - Kurri STS to Rutherford ZS | 33 | 50.1 | 31.1
Feeder KU13 - Kurri STS to Telarah ZS | 33 | 30.1 | 24.1
Feeder 33854 - Beresfield STS to Tarro ZS | 33 | 48.1 | 34.1
Feeder 33859 - Beresfield STS to Thornton ZS | 33 | 59.1 | 34.1
Feeder 33874(1) - Beresfield STS to 33874 Tee 1 | 33 | 59.1 | 37.1
Feeder 33874(2) - 33874 Tee 1 to Metford ZS | 33 | 91.1 | 37.1
Feeder 33874(3) - 33874 Tee 1 to ABS-16832 | 33 | 64.1 | 0
Feeder 33884 - Beresfield STS to Abel Mine | 33 | 20.1 | 0
Feeder 33899 - Beresfield STS to Thornton ZS | 33 | 59.1 | 34.1
Feeder 33904(1) - Beresfield STS to 33904 Tee 1 | 33 | 61.1 | 39.1
Feeder 33904(2) - 33904 Tee 1 to Tarro ZS | 33 | 88.1 | 39.1
Feeder 33904(3) - 33904 Tee 1 to Beresfield PS 33kV | 33 | 11.1 | 0
Feeder 34099(1) - Thornton ZS to 34099 Tee 1 | 33 | 55.1 | 0
Feeder 34099(3) - 34099 Tee 1 to Gresford (Essential) | 33 | 6.1 | 0
Feeder 34116 - Thornton ZS to Metford ZS | 33 | 88.1 | 49.1
Newcastle Inner City Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 762 - Merewether STS to New Lambton ZS | 33 | 42.1 | 23.1
Feeder 76F - Merewether STS to New Lambton ZS | 33 | 27.1 | 17.1
Feeder H763 - Merewether STS to Tighes Hill ZS | 33 | 45.1 | 0
Feeder H764 - Merewether STS to Newcastle CBD ZS | 33 | 40.1 | 36.1
Feeder H769 - Merewether STS to Tighes Hill ZS | 33 | 45.1 | 0
Feeder H770 - Merewether STS to Newcastle CBD ZS | 33 | 33.1 | 31.1
Feeder H773 - Merewether STS to Kotara ZS | 33 | 31.1 | 0
Feeder H775 - Merewether STS to Kotara ZS | 33 | 36.1 | 0
Feeder H776 - Merewether STS to Newcastle CBD ZS | 33 | 40.1 | 0
Newcastle Ports Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 3020(1) - 3020 Tee to P:JT-87032 | 33KV | 29 | 0
Feeder 3020(2) - Koorgang STS to 3020 Tee | 33KV | 32 | 0
Feeder 3020(3) - 3020 Tee to Hexham SS | 33KV | 30 | 0
Newcastle Western Corridor Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 80252 - Argenton STS to Cardiff ZS | 33 | 49.1 | 33.1
Feeder 80258 - Argenton STS to Edgeworth ZS | 33 | 44.1 | 29.1
Feeder 80262(1) - Argenton STS to 80262 Tee 1 | 33 | 42.1 | 32.1
Feeder 80262(2) - 80262 Tee 1 to Edgeworth ZS | 33 | 60.1 | 32.1
Feeder 80266 - Argenton STS to Cardiff ZS | 33 | 46.1 | 33.1
North East Lake Macquarie Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder H766 - Merewether STS to Gateshead ZS | 33 | 70.1 | 43.1
Feeder 760 - Merewether STS to Jewells ZS | 33 | 48.1 | 29.1
Feeder 772 - Merewether STS to Gateshead ZS | 33 | 50.1 | 30.1
Feeder 3231 - Jewells ZS to Pelican ZS | 33 | 44.1 | 28.1
Feeder 3239(1) - 3239 Tee 1 to Pelican ZS | 33 | 54.1 | 29.1
Feeder 3239(2) - Gateshead ZS to 3239 Tee 1 | 33 | 37.1 | 29.1
Feeder 3240 - Pelican ZS to Swansea ZS | 33 | 24.1 | 16.1
Feeder 3431 - Gateshead ZS to Jewells ZS | 33 | 51.1 | 30.1
Feeder 3691 - Pelican ZS to Swansea ZS | 33 | 23.1 | 16.1
Feeder 34405 - Mount Hutton ZS to Croudace Bay ZS | 33 | 77.1 | 34.1
Feeder 80249 - Argenton STS to Mount Hutton ZS | 33 | 47.1 | 28.1
Feeder 80255 - Argenton STS to Croudace Bay ZS | 33 | 46.1 | 28.1
Feeder 80263 - Argenton STS to Mount Hutton ZS | 33 | 47.1 | 28.1
Port Stephens Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder TM1 - Tomago STS to Raymond Terrace ZS | 33 | 44.1 | 29.1
Feeder TM2 - Tomago STS to Nelson Bay ZS | 33 | 52.1 | 31.1
Feeder TM3 - Tomago STS to Tomago ZS | 33 | 57.1 | 42.1
Feeder TM4 - Tomago STS to Medowie ZS | 33 | 40.1 | 25.1
Feeder TM5 - Tomago STS to Tomago Sw Station | 33 | 36.1 | 23.1
Feeder TM6 - Tomago STS to Tomago ZS | 33 | 58.1 | 42.1
Feeder TM7 - Tomago STS to Williamtown ZS | 33 | 46.1 | 29.1
Feeder TM8 - Tomago STS to HDWB Tomago 33kV | 33 | 12.1 | 0
Feeder TM9 - Tomago STS to Nelson Bay ZS | 33 | 71.1 | 43.1
Feeder TM10 - Tomago STS to Williamtown ZS | 33 | 46.1 | 29.1
Feeder TM11 - Tomago STS to HDWB Tomago 33kV | 33 | 16.1 | 0
Feeder TM12 - Tomago STS to Raymond Terrace ZS | 33 | 44.1 | 29.1
Feeder TM13 - Tomago STS to Medowie ZS | 33 | 57.1 | 34.1
Feeder 3300(1) - Williamtown to 3300 Tee 1 | 33 | 59.1 | 32.1
Feeder 3300(2) - 3300 Tee 1 to Tomaree ZS | 33 | 59.1 | 31.1
Feeder 3300(3) - 3300 Tee 1 to Tanilba Bay ZS | 33 | 18.1 | 0
Feeder 3301 - Williamtown ZS to Stockton ZS | 33 | 13.1 | 10.1
Feeder 3305 - Williamtown ZS to Stockton ZS | 33 | 22.1 | 13.1
Feeder 3306 - Williamtown ZS to Williamtown RAAF | 33 | 40.1 | 24.1
Feeder 33366 - Nelson Bay ZS to Tomaree ZS | 33 | 58.1 | 36.1
Feeder 34084 - Williamtown ZS to Williamtown RAAF | 33 | 31.1 | 26.1
Feeder 81401(1) - Tanilba Bay ZS to 81401 Tee 1 | 33 | 34.1 | 0
Feeder 81401(2) - 81401 Tee 1 to Tea Gardens (Essential) | 33 | 8.1 | 0
Feeder 81401(3) - 81401 Tee 1 to Medowie ZS | 33 | 35.1 | 0
Feeder 83241(1) - Tomago Sw Station to 83241 Tee 1 | 33 | 33.1 | 21.1
Feeder 83241(3) - 83241 Tee 1 to Raymond Terrace ZS | 33 | 45.1 | 21.1
Singleton Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 33474 - Singleton North ZS to Singleton ZS | 66 | 171.1 | 85.1
Feeder 6011(1) - Singleton STS to 6011 Tee 1 | 66 | 108.1 | 73.1
Feeder 6011(2) - 6011 Tee 1 to Lemington Mine 66kV | 66 | 16.1 | 0
Feeder 6011(3) - 6011 Tee 1 6011 Tee 2 | 66 | 121.1 | 72.1
Feeder 6011(4) - 6011 Tee 2 to 6011 Tee 4 | 66 | 54.1 | 0
Feeder 6011(5) - 6011 Tee 2 to 6011 Tee 3 | 66 | 125.1 | 67.1
Feeder 6011(6) - 6011 Tee 3 to United Colliery 66kV | 66 | 42.1 | 0
Feeder 6011(7) - 6011 Tee 3 to Lemington ZS | 66 | 101.1 | 67.1
Feeder 6011(8) - 6011 Tee 4 to Wambo 66kV | 66 | 33.1 | 0
Feeder 6011(9) - 6011 Tee 4 to 6011 Tee 5 | 66 | 38.1 | 0
Feeder 6011(10) - 6011 Tee 5 to South Lemington Mine 66kV | 66 | 38.1 | 0
Feeder 6012(1) - Singleton STS to 6012 Tee 1 | 66 | 113.1 | 78.1
Feeder 6012(2) - 6012 Tee 1 to Rixs Creek Coal 66kV | 66 | 43.1 | 0
Feeder 6012(3) - 6012 Tee 1 to 6012 Tee 2 | 66 | 135.1 | 77.1
Feeder 6012(4) - 6012 Tee 2 to 6012 Tee 3 | 66 | 28.1 | 0
Feeder 6012(5) - 6012 Tee 3 to Camberwell Coal 66kV | 66 | 28.1 | 0
Feeder 6012(6) - 6012 Tee 3 to 6012 Tee 4 | 66 | 22.1 | 0
Feeder 6012(7) - 6012 Tee 4 to Glennies Creek Mine 66kV | 66 | 22.1 | 0
Feeder 6012(8) - 6012 Tee 4 to Glennies Creek Generator | 66 | 22.1 | 0
Feeder 6012(9) - 6012 Tee 2 to Singleton North ZS | 66 | 144.1 | 77.1
Feeder 6017(1) - Singleton STS to 6017 Tee 1 | 66 | 104.1 | 71.1
Feeder 6017(2) - 6017 Tee 1 Ashton Mine 66kV | 66 | 65.1 | 0
Feeder 6017(3) - 6017 Tee 1 to 6017 Tee 2 | 66 | 119.1 | 68.1
Feeder 6017(4) - 6017 Tee 2 to Glendell Mine 66kV | 66 | 73.1 | 0
Feeder 6017(5) - 6017 Tee 2 to Newdell ZS | 66 | 103.1 | 67.1
Feeder 6018(1) - Singleton STS to 6018 Tee 1 | 66 | 121.1 | 96.1
Feeder 6018(2) - 6018 Tee 1 to 6018 Tee 2 | 66 | 180.1 | 96.1
Feeder 6018(3) - 6018 Tee 2 to Mt Thorley ZS | 66 | 169.1 | 96.1
Feeder 6018(5) - 6018 Tee 1 to ABS-66226 | 66 | 39.1 | 0
Feeder 6019 - Singleton STS to Mt Thorley ZS | 66 | 133.1 | 91.1
Feeder 60200(1) - Newdell ZS to 60200 Tee 1 | 66 | 72.1 | 0
Feeder 60200(3) - 60200 Tee 1 to Ravensworth North 66kV | 66 | 72.1 | 0
Feeder 60208(1) - Newdell ZS to 60208 Tee 1 | 66 | 104.1 | 67.1
Feeder 60208(2) - 60208 Tee 1 to Coal & Allied 66kV | 66 | 24.1 | 0
Feeder 60208(3) - 60208 Tee 1 to 60208 Tee 2 | 66 | 104.1 | 69.1
Feeder 60208(4) - 60208 Tee 2 to 60208 Tee 3 | 66 | 119.1 | 69.1
Feeder 60208(5) - 60208 Tee 3 to Lemington ZS | 66 | 126.1 | 68.1
Feeder 60208(6) - 60208 Tee 3 to Hunter Valley CPP 66kV | 66 | 93.1 | 0
Feeder 60208(7) - 60208 Tee 2 to ABS-63327 | 66 | 104.1 | 0
Feeder 66011(1) - Singleton North ZS to 66011 Tee 3 | 66 | 172.1 | 90.1
Feeder 66011(2) 66011 Tee 3 to 66011 Tee 5 | 66 | 68.1 | 0
Feeder 66011(3) - 66011 Tee 5 to Mitchells Flat ZS | 66 | 40.1 | 0
Feeder 66011(4) - 66011 Tee 5 to Branxton ZS | 66 | 46.1 | 0
Feeder 66011(5) - 66011 Tee 2 to 66011 Tee 3 | 66 | 145.1 | 90.1
Feeder 66011(6) - 66011 Tee 2 to 66011 Tee 4 | 66 | 32.1 | 0
Feeder 66011(7) - 66011 Tee 4 to Bulga Coal 66kV | 66 | 32.1 | 0
Feeder 66011(8) - 66011 Tee 4 to ABS-66066 | 66 | 32.1 | 0
Feeder 66011(9) - 66011 Tee 1 to 66011 Tee 2 | 66 | 119.1 | 91.1
Feeder 66011(10) Mt Thorley ZS to 66011 Tee 1 | 66 | 111.1 | 91.1
Feeder 66011(11) - 66011 Tee 1 to ABS-66021 | 66 | 96.1 | 0
Feeder 66090(1) - Mt Thorley ZS to 66090 Tee 1 | 66 | 102.1 | 0
Feeder 66090(2) - 66090 Tee 1 to Warkworth Mine 66kV | 66 | 68.1 | 0
Feeder 66090(3) - 66090 Tee 1 to ABS-66079 | 66 | 96.1 | 0
Feeder 66092(1) - Mt Thorley ZS to 66092 Tee 1 | 66 | 17.1 | 0
Feeder 66092(3) - 66092 Tee 1 to Mt Thorley Operations 66kV | 66 | 17.1 | 0
Feeder KU12(1) - Kurri STS to KU12 Tee | 66 | 40.1 | 0
Feeder KU12(1) - KU12 Tee to Branxton ZS | 66 | 40.1 | 0
Feeder KU12(1) - KU12 Tee to ABS-66066 | 66 | 40.1 | 0
Upper Hunter Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 6022 - Mitchell Line STS to Aberdeen ZS | 66 | 78.1 | 63.1
Feeder 6023(1) - Mitchell Line STS to 6023 Tee | 66 | 70.1 | 0
Feeder 6023(2) - 6023 Tee to Mount Arthur Coal 66kV | 66 | 68.1 | 0
Feeder 6025(1) - Mitchell Line STS to 6025 Tee | 66 | 69.1 | 62.1
Feeder 6025(3) - 6025 Tee to Denman ZS | 66 | 89.1 | 62.1
Feeder 6027(1) - Mitchell Line STS to 6027 Tee | 66 | 67.1 | 62.1
Feeder 6027(2) - 6027 Tee to Denman ZS | 66 | 87.1 | 61.1
Feeder 6027(3) - 6027 Tee to ABS-49229 | 66 | 63.1 | 0
Feeder 6028(1) - Mitchell Line STS to 6028 Tee 1 | 66 | 75.1 | 63.1
Feeder 6028(3) - 6028 Tee 1 to Tee 2 | 66 | 74.1 | 63.1
Feeder 6028(4) - 6028 Tee 2 to Bengalla Mine 66kV | 66 | 67.1 | 0
Feeder 6028(5) - 6028 Tee 2 to 6028 Tee 3 | 66 | 73.1 | 63.1
Feeder 6028(6) - 6028 Tee 3 to Mt Pleasant 66kV | 66 | 65.1 | 0
Feeder 6028(7) - 6028 Tee 3 to Tee 4 | 66 | 76.1 | 63.1
Feeder 6028(8) - 6028 Tee 4 to Dartbrook Coal 66kV | 66 | 63.1 | 0
Feeder 6028(9) - 6028 Tee 4 to Scone ZS | 66 | 100.1 | 63.1
Feeder 60334(2) - Denman ZS to 60334 Tee 1 | 33 | 28.1 | 0
Feeder 60334(3) - 60334 Tee 1 to Baerami ZS | 33 | 4.1 | 0
Feeder 60334(4) - 60334 Tee 1 to Merriwa ZS | 33 | 6.1 | 0
Feeder 82244 - Aberdeen ZS to Scone ZS | 66 | 107.1 | 62.1
Feeder 89047(1) - Scone ZS to 89047 Tee 1 | 33 | 21.1 | 0
Feeder 89047(2) - 89047 Tee 1 to 89047 Tee 2 | 33 | 20.1 | 0
Feeder 89047(3) - 89047 Tee 1 to Moonan ZS | 33 | 5.1 | 0
Feeder 89047(4) - 89047 Tee 2 to Rouchel ZS | 33 | 20.1 | 0
Feeder 89047(5) - 89047 Tee 2 to Glenbawn Hydro | 33 | 20.1 | 0
Feeder 89047(6) - Rouchel ZS to LB-32030 | 33 | 19.1 | 0
Feeder 89136 - Denman ZS to Mangoola Mine | 66 | 74.1 | 0
West Lake Macquarie Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 3710(1) - Avondale ZS to 3710 Tee 1 | 33 | 33.1 | 20.1
Feeder 3710(2) - Cooranbong ZS to 3710 Tee 1 | 33 | 40.1 | 20.1
Feeder 3710(3) - 3710 Tee 1 to 3710 Tee 2 | 33 | 31.1 | 0
Feeder 3710(4) - 3710 Tee 2 to P:GW-60212 | 33 | 31.1 | 0
Feeder H730(1) - Awaba STS to H730 Tee 1 | 33 | 29.1 | 18.1
Feeder H730(2) - H730 Tee 1 to LB-10919 | 33 | 20.1 | 0
Feeder H730(3) - H730 Tee 1 to H730 Tee 2 | 33 | 26.1 | 18.1
Feeder H730(4) - H730 Tee 2 to DS65600 | 33 | 20.1 | 0
Feeder H730(5) - H730 Tee 2 to H730 Tee 3 | 33 | 42.1 | 18.1
Feeder H730(6) - H730 Tee 3 to DS33165 | 33 | 20.1 | 0
Feeder H730(7) - H730 Tee 3 to Awaba State Mine 33kV | 33 | 42.1 | 18.1
Feeder H734 - Awaba STS to Newstan Colliery 33kV | 33 | 50 | 42
Feeder H735 - Awaba STS to Newstan Colliery 33kV | 33 | 50.1 | 29.1
Feeder H738(2) - H738 Tee to Awaba State Mine 33kV | 33 | 42.1 | 18.1
Feeder H738(3) - H738 Tee to DS33166 | 33 | 30.1 | 0
Feeder 752 - Awaba STS to SRA Awaba 33kV | 33 | 27.1 | 0
Feeder H783(1) - Eraring STS to H783 Tee | 33 | 56.1 | 22.1
Feeder H783(2) - H783 Tee to Avondale ZS | 33 | 35.1 | 22.1
Feeder 784 - Eraring STS to Cooranbong ZS | 33 | 54.1 | 20.1
Feeder H785(1) - Eraring STS to H785 Tee 1 | 33 | 34.1 | 32.1
Feeder H785(2) - H785 Tee 1 to DS33106 | 33 | 31.1 | 0
Feeder H785(3) - H785 Tee 1 to H785 Tee 2 | 33 | 37.1 | 32.1
Feeder H785(4) - H785 Tee 2 to ABS-2413 | 33 | 33.1 | 0
Feeder H785(5) - H785 Tee 2 to H785 Tee 3 | 33 | 39.1 | 32.1
Feeder H785(6) - H785 Tee 3 to ABS-2423 | 33 | 33.1 | 0
Feeder H785(7) - H785 Tee 3 to H785 Tee 4 | 33 | 41.1 | 32.1
Feeder H785(8) - H785 Tee 4 to ABS-24Y1 | 33 | 32.1 | 0
Feeder H785(9) - H785 Tee 4 to H785 Tee 5 | 33 | 45.1 | 32.1
Feeder H785(10) - H785 Tee 5 to ABS-24X1 | 33 | 32.1 | 0
Feeder H785(11) - H785 Tee 5 to H785 Tee 6 | 33 | 50.1 | 31.1
Feeder H785(12) - H785 Tee 6 to ABS-2433 | 33 | 32.1 | 0
Feeder H785(13) - H785 Tee 6 to Myuna ZS | 33 | 62.1 | 31.1
Feeder H786(1) - Eraring STS to H786 Tee | 33 | 33.1 | 30.1
Feeder H786(2) - H786 Tee to Myuna ZS | 33 | 44.1 | 30.1
Feeder H786(3) - H786 Tee to DS33152 | 33 | 31.1 | 0
Feeder 77M(1) - Morisset Annex to 77M Tee 1 | 33 | 35.1 | 0
Feeder 77M(2) - 77M Tee 1 to LB-78049 | 33 | 31.1 | 0
Feeder 77M(3) - 77M Tee 1 to 77M Tee 2 | 33 | 31.1 | 0
Feeder 77M(4) - 77M Tee 2 to 77M Tee 3 | 33 | 31.1 | 0
Feeder 77M(5) - 77M Tee 2 to Mandalong South Mine 33kV | 33 | 30.1 | 0
Feeder 77M(6) - 77M Tee 3 to P:MG-30242 | 33 | 31.1 | 0
Feeder 77M(7) - 77M Tee 3 to Mandalong Mine 33kV | 33 | 31.1 | 0
Inner Metropolitan Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
FEEDER 202: [DRUMMOYNE - ROZELLE] | 132 | 219.1 | 151.1
FEEDER 203(1): [MASON PARK STSS - HOMEBUSH] | 132 | 508.1 | 132.1
FEEDER 203(2): [HOMEBUSH - HOMEBUSH STS] | 132 | 246.1 | 133.1
FEEDER 203(3): [HOMEBUSH - DRUMMOYNE] | 132 | 137.1 | 0
FEEDER 204: [MASON PARK - DRUMMOYNE] | 132 | 226.1 | 168.1
FEEDER 240(1): [CHULLORA - CHULLORA] | 132 | 267.1 | 253.1
FEEDER 240(2): [POTTS HILL - CHULLORA] | 132 | 294.1 | 244.1
FEEDER 240(3): [ROOKWOOD BSP - CHULLORA] | 132 | 319.1 | 287.1
FEEDER 241(1): [CHULLORA - CHULLORA] | 132 | 270.1 | 251.1
FEEDER 241(2): [POTTS HILL - CHULLORA] | 132 | 294.1 | 243.1
FEEDER 241(3): [ROOKWOOD BSP - CHULLORA] | 132 | 318.1 | 288.1
FEEDER 245: [KURNELL - BUNNERONG] | 132 | 195.1 | 194.1
FEEDER 246: [KURNELL - BUNNERONG] | 132 | 195.1 | 194.1
FEEDER 260: [BEACONSFIELD BSP - ZETLAND] | 132 | 19.1 | 0
FEEDER 261: [BEACONSFIELD BSP - ZETLAND] | 132 | 21.1 | 0
FEEDER 262: [DOUBLE BAY - CLOVELLY] | 132 | 160.1 | 0
FEEDER 264: [BEACONSFIELD BSP - KINGSFORD] | 132 | 129.1 | 129.1
FEEDER 265: [BUNNERONG - MAROUBRA] | 132 | 300.1 | 226.1
FEEDER 26C: [KINGSFORD - CLOVELLY] | 132 | 236.1 | 0
FEEDER 270: [MAROUBRA - KINGSFORD] | 132 | 282.1 | 220.1
FEEDER 280: [PORT HACKING STS - KIRRAWEE] | 132 | 417.1 | 253.1
FEEDER 281: [KIRRAWEE - CRONULLA] | 132 | 394.1 | 264.1
FEEDER 284: [SYDNEY SOUTH BSP - MENAI] | 132 | 255.1 | 191.1
FEEDER 285: [MENAI - ENGADINE] | 132 | 116.1 | 0
FEEDER 286: [ENGADINE - SRA (HEATHCOTE)] | 132 | 116.1 | 0
FEEDER 289: [ENGADINE - PORT HACKING STS] | 132 | 249.1 | 182.1
FEEDER 293: [BANKSTOWN - GREENACRE PARK] | 132 | 259.1 | 216.1
FEEDER 294: [BANKSTOWN - GREENACRE PARK] | 132 | 271.1 | 216.1
FEEDER 295: [POTTS HILL - SEFTON] | 132 | 234.1 | 0
FEEDER 296(1): [ROOKWOOD BSP - SEFTON] | 132 | 234.1 | 0
FEEDER 296(2): [SEFTON - SEFTON] | 132 | 234.1 | 0
FEEDER 905: [KOGARAH - ROCKDALE] | 132 | 323.1 | 264.1
FEEDER 906: [CANTERBURY - MARRICKVILLE] | 132 | 235.1 | 225.1
FEEDER 907: [ROCKDALE - CANTERBURY] | 132 | 308.1 | 276.1
FEEDER 90P/1: [HAYMARKET - CITY SOUTH] | 132 | 0.1 | 0.1
FEEDER 90P/2: [CITY CENTRAL - CITY SOUTH] | 132 | 102.1 | 0.1
FEEDER 90R: [CAMPBELL ST - DOUBLE BAY] | 132 | 175.1 | 0
FEEDER 90T/1: [HAYMARKET - GREEN SQUARE] | 132 | 63.1 | 0.1
FEEDER 90T/2: [ALEXANDRIA - GREEN SQUARE] | 132 | 0.1 | 0.1
FEEDER 90V/1: [HAYMARKET - CITY SOUTH] | 132 | 0.1 | 0.1
FEEDER 90V/2: [CITY CENTRAL - CITY SOUTH] | 132 | 105.1 | 0.1
FEEDER 90W/1: [HAYMARKET - CITY SOUTH] | 132 | 0.1 | 0.1
FEEDER 90W/2: [CITY CENTRAL - CITY SOUTH] | 132 | 103.1 | 0.1
FEEDER 90W/4: [ROZELLE - PYRMONT] | 132 | 134.1 | 0
FEEDER 90X: [MASON PARK STSS - MEADOWBANK] | 132 | 296.1 | 262.1
FEEDER 90Y: [BEACONSFIELD BSP - BELMORE PARK] | 132 | 43.1 | 0.1
FEEDER 90Z/1: [HAYMARKET - CITY SOUTH] | 132 | 21.1 | 0.1
FEEDER 90Z/2: [CITY SOUTH - CITY NORTH] | 132 | 160.1 | 70.1
FEEDER 910(1): [SYDNEY SOUTH BSP - SYDNEY SOUTH] | 132 | 378.1 | 242.1
FEEDER 910(2): [SYDNEY SOUTH - CANTERBURY] | 132 | 283.1 | 242.1
FEEDER 911(1): [SYDNEY SOUTH BSP - SYDNEY SOUTH] | 132 | 381.1 | 241.1
FEEDER 911(2): [SYDNEY SOUTH - STRATHFIELD SOUTH] | 132 | 310.1 | 241.1
FEEDER 912: [SYDNEY SOUTH BSP - PORT HACKING STS] | 132 | 308.1 | 223.1
FEEDER 913: [STRATHFIELD SOUTH - CANTERBURY] | 132 | 311.1 | 236.1
FEEDER 914: [SYDNEY SOUTH BSP - BANKSTOWN] | 132 | 374.1 | 295.1
FEEDER 915: [SYDNEY SOUTH BSP - BANKSTOWN] | 132 | 374.1 | 295.1
FEEDER 916(1): [SYDNEY SOUTH BSP - CRONULLA] | 132 | 588.1 | 449.1
FEEDER 916(2): [KURNELL - CRONULLA] | 132 | 644.1 | 450.1
FEEDER 916(3): [CRONULLA - CRONULLA] | 132 | 332.1 | 238.1
FEEDER 917(1): [SYDNEY SOUTH BSP - GWAWLEY BAY] | 132 | 495.1 | 448.1
FEEDER 917(2): [GWAWLEY BAY - GWAWLEY BAY] | 132 | 293.1 | 0
FEEDER 917(3): [KURNELL - GWAWLEY BAY] | 132 | 734.1 | 451.1
FEEDER 91A: [BEACONSFIELD BSP - ST PETERS] | 132 | 0.1 | 0.1
FEEDER 91B: [BEACONSFIELD BSP - ST PETERS] | 132 | 0.1 | 0.1
FEEDER 91C: [PEAKHURST - HURSTVILLE NORTH] | 132 | 380.1 | 355.1
FEEDER 91F: [SYDNEY SOUTH BSP - PEAKHURST] | 132 | 215.1 | 215.1
FEEDER 91G: [HAYMARKET - CITY NORTH] | 132 | 48.1 | 0.1
FEEDER 91H/1: [HURSTVILLE NORTH - HURSTVILLE NORTH] | 132 | 384.1 | 239.1
FEEDER 91J: [SYDNEY SOUTH BSP - PEAKHURST] | 132 | 214.1 | 214.1
FEEDER 91R: [PEAKHURST - HURSTVILLE NORTH] | 132 | 381.1 | 355.1
FEEDER 91T: [CAMPBELL ST - ROSE BAY] | 132 | 296.1 | 200.1
FEEDER 91U: [MARRICKVILLE - BEACONSFIELD BSP] | 132 | 68.1 | 68.1
FEEDER 91W: [HURSTVILLE NORTH - KOGARAH] | 132 | 384.1 | 195.1
FEEDER 91X/1: [BEACONSFIELD BSP - MARRICKVILLE] | 132 | 16.1 | 16.1
FEEDER 91X/2: [CHULLORA - MARRICKVILLE] | 132 | 149.1 | 111.1
FEEDER 91Y/1: [BEACONSFIELD BSP - MARRICKVILLE] | 132 | 16.1 | 16.1
FEEDER 91Y/2: [MARRICKVILLE - CHULLORA] | 132 | 149.1 | 111.1
FEEDER 926(1): [SYDNEY NORTH - CARLINGFORD] | 132 | 734.1 | 400.1
FEEDER 926(3): [CARLINGFORD - MASON PARK] | 132 | 494.1 | 399.1
FEEDER 927(1): [SYDNEY NORTH - CARLINGFORD] | 132 | 738.1 | 400.1
FEEDER 927(3): [CARLINGFORD - HOMEBUSH BAY] | 132 | 494.1 | 398.1
FEEDER 928/1: [SURRY HILLS - DALLEY ST] | 132 | 107.1 | 90.1
FEEDER 92A(1): [SYDNEY NORTH - MACQUARIE PARK] | 132 | 831.1 | 554.1
FEEDER 92A(2): [LANE COVE - MACQUARIE PARK] | 132 | 657.1 | 313.1
FEEDER 92A(3): [MACQUARIE PARK - MACQUARIE PARK] | 132 | 333.1 | 194.1
FEEDER 92B(1): [SYDNEY NORTH - MACQUARIE PARK] | 132 | 827.1 | 506.1
FEEDER 92B(2): [LANE COVE - MACQUARIE PARK] | 132 | 658.1 | 321.1
FEEDER 92B(3): [MACQUARIE PARK - MACQUARIE STS] | 132 | 395.1 | 294.1
FEEDER 92C: [CHULLORA - ST PETERS] | 132 | 151.1 | 120.1
FEEDER 92E: [HAYMARKET - CITY NORTH] | 132 | 48.1 | 0.1
FEEDER 92F: [MASON PARK STSS - TOP RYDE] | 132 | 309.1 | 264.1
FEEDER 92G: [LANE COVE STSS - TOP RYDE] | 132 | 403.1 | 247.1
FEEDER 92H: [MACQUARIE PARK - MACQUARIE STS] | 132 | 491.1 | 296.1
FEEDER 92J: [LANE COVE STSS - MEADOWBANK] | 132 | 398.1 | 247.1
FEEDER 92M/3: [CAMPBELL ST - SURRY HILLS] | 132 | 50.1 | 0.1
FEEDER 92P: [BEACONSFIELD BSP - BELMORE PARK] | 132 | 92.1 | 0.1
FEEDER 92X: [ST PETERS - CHULLORA] | 132 | 148.1 | 120.1
FEEDER 935: [HOMEBUSH BAY - MASON PARK] | 132 | 406.1 | 0.1
FEEDER 93C: [HAYMARKET - CITY NORTH] | 132 | 48.1 | 0.1
FEEDER 93H: [BELMORE PARK - HAYMARKET] | 132 | 0.1 | 0.1
FEEDER 9F6: [MARRICKVILLE - BEACONSFIELD BSP] | 132 | 57.1 | 57.1
FEEDER 9FF: [BEACONSFIELD - BUNNERONG] | 132 | 226.1 | 191.1
FEEDER 9P2: [MASON PARK - CROYDON] | 132 | 300.1 | 204.1
FEEDER 9P8: [CROYDON - LEICHHARDT] | 132 | 374.1 | 180.1
FEEDER 9P9: [ROZELLE - LEICHHARDT] | 132 | 273.1 | 153.1
FEEDER 9R8: [ROSE BAY - WAVERLEY] | 132 | 379.1 | 0.1
FEEDER 9RF: [BEACONSFIELD BSP - ALEXANDRIA] | 132 | 0.1 | 0.1
FEEDER 9S2: [HAYMARKET - BEACONSFIELD BSP] | 132 | 88.1 | 0.1
FEEDER 9S4: [HAYMARKET - BEACONSFIELD BSP] | 132 | 53.1 | 0.1
FEEDER 9S6/1: [HAYMARKET - PYRMONT] | 132 | 110.1 | 0.1
FEEDER 9S6/2: [PYRMONT - DARLING HARBOUR] | 132 | 239.1 | 0.1
FEEDER 9S6/3: [CITY CENTRAL - DARLING HARBOUR] | 132 | 81.1 | 0.1
FEEDER 9S6/4: [CITY CENTRAL - CITY NORTH] | 132 | 81.1 | 0
FEEDER 9S9/1: [HAYMARKET - PYRMONT] | 132 | 110.1 | 0.1
FEEDER 9S9/2: [PYRMONT - DARLING HARBOUR] | 132 | 239.1 | 0
FEEDER 9SA: [CAMPBELL ST - BEACONSFIELD BSP] | 132 | 100.1 | 0.1
FEEDER 9SB/1: [BELMORE PARK - SURRY HILLS ANNEXE] | 132 | 24.1 | 0.1
FEEDER 9SB/2: [SURRY HILLS ANNEXE - DOUBLE BAY] | 132 | 141.1 | 0
FEEDER 9SC: [HAYMARKET - CAMPBELL ST] | 132 | 1.1 | 0.1
FEEDER 9SE: [BEACONSFIELD BSP - GREEN SQUARE] | 132 | 0.1 | 0.1
FEEDER 9SL: [BELMORE PARK - WAVERLEY] | 132 | 275.1 | 0.1
Central Coast Transmission Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 268 - Ourimbah STS to Wamberal ZS | 132 | 132.1 | 0
Feeder 94L - Tuggerah BSP to Berkeley Vale ZS | 132 | 274.1 | 0
Feeder 951 - West Gosford ZS to Ourimbah STS | 132 | 336.1 | 234.1
Feeder 954 - Tuggerah BSP to Berkeley Vale ZS | 132 | 243.1 | 0
Feeder 956 - West Gosford ZS to Gosford STS | 132 | 278.1 | 254.1
Feeder 957/1 - 957 Tee 1 to Ourimbah STS | 132 | 238.1 | 137.1
Feeder 957/2 - 957 Tee 1 to Morisset ZS | 132 | 181.1 | 132.1
Feeder 957/3 - Vales Point PS to 957 Tee 1 | 132 | 137.1 | 128.1
Feeder 958 - Tuggerah BSP to Gosford STS | 132 | 360.1 | 236.1
Feeder 95C - Tuggerah BSP to Ourimbah STS | 132 | 459.1 | 250.1
Feeder 95E - Gosford STS to Somersby ZS | 132 | 226.1 | 138.1
Feeder 95T - Vales Point PS to Lake Munmorah ZS | 132 | 197.1 | 0
Feeder 95Z - Somersby ZS to Mt Colah SS | 132 | 154.1 | 149.1
Feeder 97E - Munmorah STS to Charmhaven ZS | 132 | 358.1 | 256.1
Feeder 97U - Munmorah PS to Munmorah STS | 132 | 410.1 | 256.1
Feeder 98B - Charmhaven ZS to Wyong ZS | 132 | 376.1 | 256.1
Feeder 99C - Tuggerah BSP to Wyong ZS | 132 | 396.1 | 256.1
Lower Hunter Transmission Area
Feeder name | Voltage (KV) | Generator Hosting Capacity (MW)
|  | N | N-1
Feeder 950 - Newcastle BSP to Jesmond ZS | 132 | 212.1 | 149.1
Feeder 952 - Newcastle BSP to Rathmines ZS | 132 | 264.1 | 162.1
Feeder 955 - Singleton STS to Rothbury ZS | 132 | 162.1 | 0
Feeder 95A - Newcastle BSP to Awaba STS | 132 | 221.1 | 150.1
Feeder 95F - Muswellbrook STS to Mitchell Line STS | 132 | 234.1 | 127.1
Feeder 95G - Awaba STS to Toronto West ZS | 132 | 301.1 | 149.1
Feeder 95H - Muswellbrook BSP to Muswellbrook STS | 132 | 358.1 | 180.1
Feeder 95L - Hydro Aluminium to Kurri STS | 132 | 439.1 | 285.1
Feeder 95M - Muswellbrook BSP to Mitchell Line STS | 132 | 408.1 | 230.1
Feeder 95R - Kurri STS to Rothbury ZS | 132 | 165.1 | 0
Feeder 95U - Muswellbrook BSP to Singleton STS | 132 | 460.1 | 269.1
Feeder 95X - Mitchell Line STS to Singleton STS | 132 | 451.1 | 247.1
Feeder 95Y(1) - 95Y Tee 1 to Eraring STS Tx1 | 132 | 166.1 | 151.1
Feeder 95Y(2) - 95Y Tee 1 to Morisset ZS | 132 | 250.1 | 129.1
Feeder 95Y(3) - Rathmines ZS to 95Y Tee 1 | 132 | 263.1 | 151.1
Feeder 960(1) - Newcastle BSP to 960 Tee 1 | 132 | 875.1 | 337.1
Feeder 960(2) - 960 Tee 1 to Charlestown ZS | 132 | 428.1 | 240.1
Feeder 960(3) - 960 Tee 1 to Argenton STS | 132 | 527.1 | 278.1
Feeder 961(1) - Newcastle BSP to 961 Tee 1 | 132 | 875.1 | 336.1
Feeder 961(2) - 961 Tee 1 to Merewether STS | 132 | 375.1 | 210.1
Feeder 961(3) - 961 Tee 1 to Argenton STS | 132 | 527.1 | 278.1
Feeder 963 - Tomago BSP to Taree | 132 | 186.1 | 186.1
Feeder 96A - Newcastle BSP to Kurri STS | 132 | 490.1 | 285.1
Feeder 96B - Newcastle BSP to Hydro Aluminium | 132 | 478.1 | 285.1
Feeder 96E - Kurri ZS to Kurri STS | 132 | 316.1 | 244.1
Feeder 96J - Maryland ZS to Waratah STS | 132 | 266.1 | 149.1
Feeder 96U - Newcastle BSP to Kurri ZS | 132 | 409.1 | 245.1
Feeder 96W - Newcastle BSP to Hydro Aluminium | 132 | 482.1 | 286.1
Feeder 96X - Waratah West BSP to Kooragang STS | 132 | 290.1 | 215.1
Feeder 96Y - Waratah West BSP to Mayfield West ZS | 132 | 253.1 | 216.1
Feeder 96Z - Newcastle BSP to Maryland ZS | 132 | 198.1 | 150.1
Feeder 97M - Mayfield West ZS to Kooragang STS | 132 | 366.1 | 223.1
Feeder 97W - Mayfield West ZS to Onesteel | 132 | 109.1 | 0
Feeder 97Z - Mayfield West ZS to Onesteel | 132 | 109.1 | 0
Feeder 98A - Tomago BSP to Tomago STS | 132 | 242.1 | 162.1
Feeder 98N - Tomago BSP to Beresfield STS | 132 | 196.1 | 125.1
Feeder 98R - Tomago BSP to Beresfield STS | 132 | 278.1 | 162.1
Feeder 99Y - Kurri STS to Beresfield STS | 132 | 267.1 | 161.1
Feeder 9F3 - Rathmines ZS to Eraring STS | 132 | 160.1 | 145.1
Feeder 9F4 - Tomago BSP to Tomago STS | 132 | 401.1 | 197.1
Feeder 9F5 - Jesmond ZS to Waratah STS | 132 | 288.1 | 149.1
Feeder 9F8 - Merewether STS to Broadmeadow ZS | 132 | 365.1 | 233.1
Feeder 9F9 - Charlestown ZS to Merewether STS | 132 | 392.1 | 232.1
Feeder 9FC - Toronto West ZS to Rathmines ZS | 132 | 252.1 | 149.1
Feeder 9N9(1) - Broadmeadow ZS to 9N9 Tee 1 | 132 | 371.1 | 226.1
Feeder 9N9(2) - Waratah BSP to 9N9 Tee 1 | 132 | 408.1 | 226.1
Feeder 9NA - Newcastle BSP to Beresfield STS | 132 | 430.1 | 218.1